## (A1)외형도 IPSS-415SS(-F)
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 최대양수량 (L/h) | 19,200 (0.5m시) | 모 터 부 | 정 격 출 력 (㎾) | 0.4
| 흡 상 고 (m) | 0 |  | 정 격 전 압 (V) | 220
| 압 상 고 (m) | 13 |  | 정 격 주 파 수 (Hz) | 60
| 흡 입 경 (mm) | - |  | 회 전 수 (rpm) | 3400
| 토 출 경 (mm) | 50A |  | 모 터 Type | 단상2극
(단위 : mm)
-F: 자동형(Float S/W)
|  |  | PUMP Type |  | 볼류우트형
|  |  | 형 식 |  | IPSS-415SS(F)

## (A2)외형도 IPSS-415SS-FL
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 최대양수량 (L/h) | 19,200 (0.5m시) | 모 터 부 | 정 격 출 력 (㎾) | 0.4
| 흡 상 고 (m) | 0 |  | 정 격 전 압 (V) | 220
| 압 상 고 (m) | 13 |  | 정 격 주 파 수 (Hz) | 60
| 흡 입 경 (mm) | - |  | 회 전 수 (rpm) | 3400
| 토 출 경 (mm) | 50A |  | 모 터 Type | 단상2극
(단위 : mm)
-FL: 자동형(Level S/W)
|  |  | PUMP Type |  | 볼류트형
|  |  | 형 식 |  | IPSS-415SS-FL

## 단면도
펌 프 단 면 도
NO | 부 품 명 | 재 질 | NO | 부 품 명 | 재 질
1 | 손 잡 이 | 복합PP | 11 | 케 이 싱 | SSC 13
2 | 헤 드 | SSC 13 | 12 | 오일씰 | -
3 | 콘덴서 | PBT | 13 | 임펠러 | SSC 13
4 | 브라켓트 | ALDC | 14 | 흡입커버 | STS-304
5 | 베어링 | 6202zz | 15 | 스테레이너 | STS-304
6 | 모터프레임 | GC-200 | 16 | 토출구플랜지 | SSC 13
7 | 모터샤프트 | STS-316+SB41B | 17 | 전원코드선 | 60245 IEC-57
8 | 스테이터조립 | - |  |  | -
9 | 베어링 | 6203zz
10 | 메케니컬씰 | Sic/Sic
|  |  | PUMP Type |  | 볼류우트형
|  |  | 형 식 |  | IPSS-415SS(F,FL)

## data sheet
PUMP DATA SHEET
Model | IPSS-415SS(F/FL) | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity
OPERATING CONDITION
Liquid | Water | Flow | 180 L/min at Ht=7m
Pumping Temp | 0℃ ~ 40℃ | Suct. Head | 0m
Specific Gravity | 1 | Disch. Head | 13m
Vapor Pressure | ㎏/㎠A | Total Head | 13m
Viscosity | 5 cP
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
□ Horizontal ■ Vertical |  | Efficiency |  |  | (Parts' Name) | Symbol㉿
Number of Stages | 1 Stage | Rated Power | 400W |  | Impeller | SSC 13
Speed | 3400 | NPSHre | mAq |  | Shaft | SB41B+STS316
Rotation | ■ CW, □ CCW (viewed from pump head) |  |  |  | Casing | SSC 13
Flange | Size(Dia) | Rating | Face | Position | Frame | SSC 13
Suction | ㎜ |  | □ FF, □ RF | □TOP □Side | Head | SSC 13
Discharge | 50A |  | □ FF, ■ RF | □TOP ■Side | Flange | SSC 13
Impeller Type | Semi-Open | ■ Single Suct □ Double Suct |  | HYDROSTATIC | Power Cable | 60245 IEC-57
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | ㎏/㎠ | Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Frame | ㎏/㎠ | Min
Shaft Sleeve | ■ Yes □ No
Discharge Type | ■ Hose Connection □ Flange Connection |  |  | TESTING
Struction of Inlet | □ Stand ■ Strainer |  |  | (Items) | (self test) | (Witness)
Struction of outlet | □ Elbow ■ Hose Coupling ■ Flange Coupling |  |  | Run Perform | ■ Yes □ No | □ Yes ■ No
Bearing(Upper) | 6202 zz | Bearing(Lower) | 6203 zz | Hydrostatic | ■ Yes □ No | □ Yes ■ No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller
Maker | HANIL ELEC |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 400W |  |  |  | Casing
Pole&Speed | 2P 3400rpm | Insulation Class | ■ E □ B |  | Bearing
Mechanical Seal | Maker | EKK | Model & Size | φ14 | M/Seal
| Type | ED560-14 | Cooler | ■ Yes □ No | Name Plate
ACCESSORIES
■ Companion Flange
□ Guide Pipe |  |  |  |  | WEIGHT | (비자동/자동)
□ Special Tools |  |  |  |  | Pump | 19.3kg/19.6Kg
□ Spare Parts |  |  |  |  | Adapter
■ Hose Coupling |  |  |  |  | Total Wt.(net) | 19.3kg/19.6Kg

## test report
PUMP TEST REPORT
※SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(L/min) | 180 / Ht=7m |  | Phase(φ) |  | 1 | Out Put | 0.4 (㎾)
Total Head(m) | 13 |  | Pole(p) |  | 2 | Freq | 60 (Hz)
disch(A) | 50A |  | Volt(v) |  | 220 | Maker | HANIL
Model | IPSS-415SS(-F/-FL) |  | Customer
※ PERFORMANCE DATA (Test by Ks B 6301)
Capacity(ℓ/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | Input(kw) | Voltage(V) | Current(A)
0 | 14 | 0.3927 | 0 | 0 | 0.561 | 220 | 2.62
130 | 12 | 0.5635 | 0.25428 | 45.1251 | 0.805 | 220 | 3.76
180 | 10 | 0.5859 | 0.2934 | 50.0768 | 0.837 | 220 | 3.91
222 | 8 | 0.5817 | 0.28949 | 49.7659 | 0.831 | 220 | 3.88
243 | 7 | 0.5957 | 0.27726 | 46.5441 | 0.851 | 220 | 3.98
264 | 6 | 0.5775 | 0.25819 | 44.7086 | 0.825 | 220 | 3.86
304 | 4 | 0.6139 | 0.19821 | 32.2867 | 0.877 | 220 | 4.11
340 | 2.6 | 0.6139 | 0.14409 | 23.4716 | 0.877 | 220 | 4.12
※ PERFORMANCE CURVE