## 외형도
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 최대양수량 (L/h) | 21,600 (0.5m시) | 모 터 부 | 정 격 출 력 (㎾) | 0.75
| 흡 상 고 (m) | 0 |  | 정 격 전 압 (V) | 380
| 압 상 고 (m) | 12 |  | 정 격 주 파 수 (Hz) | 60
| 흡 입 경 (mm) | - |  | 회 전 수 (rpm) | 3400
| 토 출 경 (mm) | 50A |  | 모 터 Type | 삼상2극
(단위 : mm)
|  |  | PUMP Type |  | 볼텍스형
|  |  | 형 식 |  | IPVSS-815SS-T

## 펌프단면도
펌 프 단 면 도
NO | 부 품 명 | 재 질 | NO | 부 품 명 | 재 질
1 | 손 잡 이 | 복합PP | 11 | 오일케이싱 | SSC 13
2 | 헤 드 | SSC 13 | 12 | 오일씰 | RUBBER
3 | - | - | 13 | 케이싱패킹 | NBR
4 | 브라켓트 | ALDC | 14 | 임펠러 | SSC 13
5 | 베어링 | 6202zz | 15 | 케이싱 | SSC 13
6 | 모터프레임 | SSC 13 | 16 | 토출구플랜지 | SSC 13
7 | 모터샤프트 | STS-316+SB41B | 17 | 전원코드선 | 60245 IEC-57
8 | 스테이터조립 | -
9 | 베어링 | 6203zz
10 | 메케니컬씰 | -
|  |  | PUMP Type |  | 볼텍스형
|  |  | 형 식 |  | IPVSS-815SS-T

## data sheet
PUMP DATA SHEET
Model | IPVSS-815SS-T | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity
OPERATING CONDITION
Liquid | Water | Flow | 280 L/min at Ht=6m
Pumping Temp | 0℃ ~ 40℃ | Suct. Head | 0m
Specific Gravity | 1 | Disch. Head | 12m
Vapor Pressure | ㎏/㎠A | Total Head | 12m
Viscosity | 5 cP
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
□ Horizontal ■ Vertical |  | Efficiency |  |  | (Parts' Name) | Symbol㉿
Number of Stages | 1 Stage | Rated Power | 750W |  | Impeller | SSC-13
Speed | 3400 | NPSHre | mAq |  | Shaft | SB41B+STS316
Rotation | ■ CW, □ CCW (viewed from pump head) |  |  |  | Casing | SSC-13
Flange | Size(Dia) | Rating | Face | Position | Frame | SSC-13
Suction | - | - | □ FF, □ RF | □TOP □Side | Head | SSC-13
Discharge | 50A | - | □ FF, ■ RF | □TOP ■Side | Flange | SSC-13
Impeller Type | Semi-Open | ■ Single Suct □ Double Suct |  | HYDROSTATIC | Power Cable | 60245 IEC-57
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | ㎏/㎠ | Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Frame | ㎏/㎠ | Min
Shaft Sleeve | ■ Yes □ No
Discharge Type | ■ Hose Connection □ Flange Connection |  |  | TESTING
Struction of Inlet | ■ Stand □ Strainer |  |  | (Items) | (self test) | (Witness)
Struction of outlet | □ Elbow ■ Hose Coupling ■ Flange Coupling |  |  | Run Perform | ■ Yes □ No | □ Yes ■ No
Bearing(Upper) | 6202 zz | Bearing(Lower) | 6203 zz | Hydrostatic | ■ Yes □ No | □ Yes ■ No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 380 | 3 | 60 | Impeller
Maker | HANIL |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 750W |  |  |  | Casing
Pole&Speed | 2P 3400rpm | Insulation Class | ■ E □ B |  | Bearing
Mechanical Seal | Maker | EAGLE | Model & Size | φ14 | M/Seal
| Type | ED560-14 | Cooler | ■ Yes □ No | Name Plate
ACCESSORIES
■ Companion Flange
□ Guide Pipe |  |  |  |  | WEIGHT
□ Special Tools |  |  |  |  | Pump | 23.9 Kg
□ Spare Parts |  |  |  |  | Adapter
■ Hose Coupling |  |  |  |  | Total Wt.(net) | 23.9 Kg

## test report
PUMP TEST REPORT
※SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(L/min) | 280 / Ht=6m |  | Phase(φ) |  | 3 | Out Put | 0.75(㎾)
Total Head(m) | 12 |  | Pole(p) |  | 2 | Freq | 60 (Hz)
suct,disch(mm) | 50A |  | Volt(v) |  | 380 | Maker | HANIL
Model | IPVSS-815SS-T |  | Customer
※ PERFORMANCE DATA (Test by Ks B 6301)
Capacity(ℓ/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | Input(kw) | Voltage(V) | Current(A)
0 | 13.6 | 0.4291 | 0 | 0 | 0.613 | 380 | 1.93
155 | 10 | 0.6314 | 0.25265 | 40.0143 | 0.902 | 380 | 2.2
251 | 8 | 0.7189 | 0.3273 | 45.5284 | 1.027 | 380 | 2.33
299 | 6 | 0.7301 | 0.29242 | 40.0523 | 1.043 | 380 | 2.35
340 | 4 | 0.7203 | 0.22168 | 30.7761 | 1.029 | 380 | 2.33
366 | 2.1 | 0.7168 | 0.12528 | 17.4779 | 1.024 | 380 | 2.33
※ PERFORMANCE CURVE