## 펌프외형도
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 최대양수량 (ℓ/h) | 3300 | 모 터 부 | 정 격 출 력 (㎾) | 0.4
| 흡 상 고 (m) | 8 |  | 정 격 전 압 (V) | 220
| 압 상 고 (m) | 29 |  | 정 격 주 파 수 (Hz) | 60
| 흡 입 경 (mm) | 32 |  | 회 전 수 (rpm) | 3400
| 토 출 경 (mm) | 25 |  | 모 터 Type | 단상 2극
(단위 : mm)
|  |  |  | PUMP Type | 웨스코 Type
|  |  |  | 형 식 | PH-405W

## 펌프단면도
펌 프 단 면 도
NO | 부 품 명 | 재 질 | NO | 부 품 명 | 재 질
1 | 모터 조립 | - | 8 | 케이싱 패킹 | NBR
2 | 베 드 | P.P | 9 | 임펠러 | BsC
3 | 모터 샤프트 | SM20C+STS410 | 10 | 케이싱 커버 | MPPO
4 | 홀 더 | Aℓ-DC | 11 | 흡수파이프조립 | GC-150
5 | 미케니컬시일 | Carbon+Ceramic | 12 | 베어링 | 6202zz
6 | 보조탱크 조립 | SPCC | 13 | 베어링 | 6201zz
7 | 케이싱 조립 | GC-150+BsC | 14 | 모터 커버 | Aℓ-DC
|  |  | PUMP Type |  | 웨스코 Type
|  |  | 형 식 |  | PH-405W

## data sheet
PUMP DATA SHEET
Model | PH-405W | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■ In, □ out
OPERATING CONDITION
Liquid | Water | Flow | 40 ℓ/min at Ht=12m
Pumping Temp | 0℃ ~40℃ | Suct. Head | 8m
Specific Gravity |  | Disch. Head | 29m
Vap.Pressure | ㎏/㎠A | Total Head | 37m
Viscosity | cP
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
■Horizontal □Vertical |  | Efficiency | 26% |  | (Parts' Name) | Symbol㉿
Number of Stages | 1 Stage | Rated Power | 400 W |  | Impeller | BsC
Speed | 3400rpm | NPSHre | mAq |  | Impeller cover | MPPO
Rotation | □ CW, ■ CCW (viewed from pump head) |  |  |  | Shaft | SM20C+STS410
Flange | Size(Dia) | Rating | Face | Position | Casing | GC-150
Suction | 32㎜ |  | ■ FF, □ RF | □TOP ■Side | Suct. Flange | GC-150
Discharge | 25㎜ |  | ■ FF, □ RF | □TOP ■Side | Disch. Flange | GC-150
Impeller Type | Westco Type | ■ Single Suct □ Double Suct |  | HYDROSTATIC | Guide Vane
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | 5 ㎏/㎠ | 3 Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Pressure Tank | ㎏/㎠ | Min
Shaft Sleeve | □ Yes ■ No
Mounting | ■ Foot □ Centerline |  |  | TESTING
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) | (self test) | (Witness)
Cooling | □ Stuff. Box □ B/R Housing ■ Fan Cooling |  |  | Run Perform | ■ Yes □ No | □ Yes ■ No
R. Bearing | 6202zz | F. Bearing | 6201zz | Hydrostatic | ■ Yes □ No | □ Yes ■ No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller
Maker | HANIL PUMP LTD,. |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 400W |  |  |  | Casing Ring
Pole&Speed | 2P 3400rpm | Insulation Class | ■ E □ B |  | Bearing(R+F)
ACCESSORIES |  |  |  |  | M/Seal
■ Base Plate | □ Cast Iron ■ Plastic □ Steel Plate |  |  |  | Oil Seal
□ Unions |  |  |  |  | Coupling
□ Coupling | □ Sun Flex □ Wood □ Grid ■ No |  |  |  | Coupling Rubber
□ Pressure Gauge | □ Suct. Vacuum □ Suct. Compound □ Disch. Press ■ No |  |  |  | Name Plate
■ Plug for priming & Screw for Drain
Mechnical Seal | Maker | EKK | Model & Size | φ13.1 | WEIGHT
| Type | EA103 13A | Cooler | □ Yes ■ No | Pump/Bed | Kg
□ Companoion Flange |  |  |  |  | Driver | Kg
□ Special Tools |  |  |  |  | Total Wt.(net) | 15.8 Kg

## test report
PUMP TEST REPORT
※SPELIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(ℓ/min) | 55 |  | Phase(φ) |  | 1 | Out Put | 0.40 (㎾)
Total Head(m) | 37 |  | Pole(p) |  | 2 | Freq | 60 (Hz)
Disch Dia(mm) | 25 |  | Volt(v) |  | 220 | Maker | HANIL
Model | PH-405W |  | Customer
※ PERFOR MANCE DATA (Test by Ks B 6301)
Capacity(ℓ/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | Motor input(kw) | Vol tage(V) | Current(A)
0 | 52 | 0.624 | 0 | 0 | 1.04 | 220 | 4.97
20.8 | 36 | 0.48 | 0.12205 | 25.428 | 0.8 | 220 | 3.9
36.5 | 21 | 0.36 | 0.12494 | 34.7054 | 0.6 | 220 | 3.02
46.4 | 12 | 0.306 | 0.090758 | 29.6596 | 0.51 | 220 | 2.65
59.5 | 1 | 0.264 | 0.0096985 | 3.6737 | 0.44 | 220 | 2.31
※ PERFOR MANCE CURVE