## 펌프외형도
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 최대양수량 (ℓ/h) | 27000 | 모 터 부 | 정 격 출 력 (㎾) | 0.9
| 흡 상 고 (m) | 0 |  | 정 격 전 압 (V) | 220V/380
| 압 상 고 (m) | 24 |  | 정 격 주 파 수 (Hz) | 60
| 흡 입 경 (A) | 50 |  | 회 전 수 (rpm) | 3400
| 토 출 경 (A) | 50 |  | 모 터 Type | 삼상 2극
(단위 : mm)
|  |  | PUMP Type |  | 볼류우트형
|  |  | 형 식 |  | PASS-931SS-T

## 펌프단면도
펌 프 단 면 도
220V/380
NO | 부 품 명 | 재 질 | NO | 부 품 명 | 재 질
1 | 모터홴커버 | SPCC | 10 | 케이싱패킹 | NBR
2 | 모 터 홴 | PP | 11 | 미캐니컬실 | -
3 | 모터커버 | GC-200 | 12 | 베 어 링 | 6204 zz
4 | 콘덴서커버 | PP | 13 | 모터샤프트 | SM20C+STS316
5 | 홀 더 | SSC13 | 14 | 로터 DC | -
6 | 케 이 싱 | SSC13 | 15 | 스테이터 | S60
7 | 임 펠 러 | SSC13 | 16 | 모터프레임 | AL 압출
8 | 물빼기마개 | POM | 17 | 베 어 링 | 6203 zz
9 | 베 드 | SPCC
|  |  | PUMP Type |  | 볼류우트형
|  |  | 형 식 |  | PASS-931SS-T

## data sheet
PUMP DATA SHEET
Model | PASS-931SS-T | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■ In, □ out
OPERATING CONDITION
Liquid | Water | Flow | 315 ℓ/min at Ht=8m
Pumping Temp | 0℃ ~ 40℃ | Suct. Head | 0m
Specific Gravity | 1 | Disch. Head | 22m
Vapor Pressure | ㎏/㎠A | Total Head | 22m
Viscosity | cP
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
■ Horizontal □ Vertical |  | Efficiency |  |  | (Parts' Name) | Symbol㉿
Number of Stages | Stage | Rated Power | 900 W |  | Impeller | SSC13
Speed |  | NPSHre | mAq |  | Impeller cover
Rotation | □ CW, ■ CCW (viewed from pump head) |  |  |  | Shaft | SM20C+STS316
Flange | Size(Dia) | Rating | Face | Position | Casing | SSC13
Suction | 50A |  | □ FF, □ RF | □TOP ■Side | Suct. Flange | -
Discharge | 50A |  | □ FF, □ RF | ■TOP □Side | Disch. Flange | -
Impeller Type | open Type | ■ Single Suct □ Double Suct |  | HYDROSTATIC | Guide Vane
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | 5 ㎏/㎠ | 3 Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Pressure Tank | ㎏/㎠ | Min
Shaft Sleeve | □ Yes ■ No
Mounting | □ Foot □ Centerline |  |  | TESTING
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) | (self test) | (Witness)
Cooling | □ Stuff. Box □ B/R Housing ■ Fan Cooling |  |  | Run Perform | ■ Yes □ No | □ Yes □ No
R Bearing | 6203 zz | F Bearing | 6204 zz | Hydrostatic | ■ Yes □ No | □ Yes □ No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220/380 | 1 | 60 | Impeller
Maker | HANIL PUMP LTD,. |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 900W |  |  |  | Casing Ring
Pole&Speed | 2P 3400rpm | Insulation Class | ■ E □ B |  | Bearing(R+F)
ACCESSORIES |  |  |  |  | M/Seal
■ Base Plate | □ Cast Iron □ Plastic ■ Steel Plate |  |  |  | Oil Seal
□ Unions
□ Coupling | □ Sun Flex □ Wood □ Grid ■ No |  |  |  | Coupling
□ Pressure Gauge | □ Suct. Vacuum □ Suct. Compound □ Disch. Press ■ No |  |  |  | Coupling Rubber
■ Plug for priming & Screw for Drain |  |  |  |  | Name Plate
Mechnical Seal | Maker | EKK | Model & Size | φ14 | WEIGHT
| Type | EA103-014 | Cooler | □ Yes ■ No | Pump/Bed | Kg
□ Companoion Flange |  |  |  |  | Driver | Kg
□ Special Tools |  |  |  |  | Total Wt.(net) | 24.5 kg

## test report
PUMP TEST REPORT
※SPELIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(ℓ/min) | 315 (8m) |  | Phase(φ) |  | 1 | Rated Power | 0.9 (㎾)
Total Head(m) | 22 |  | Pole(p) |  | 2 | Freq | 60 (Hz)
suct,disch(A) | 50, 50 |  | Volt(v) |  | 380 | Maker | HANIL
Model | PASS-931SS-T |  | Customer
※ PERFOR MANCE DATA (Test by Ks B 6301)
Capacity(ℓ/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | In put(kw) | Vol tage(V) | Current(A)
0 | 23.4 | 0.6391 | 0 | 0 | 0.77 | 220 | 3.21
172 | 18 | 1.0541 | 0.50465 | 47.8748 | 1.27 | 220 | 4.23
240 | 15 | 1.1703 | 0.5868 | 50.141 | 1.41 | 220 | 4.59
294 | 12 | 1.2367 | 0.57506 | 46.4999 | 1.49 | 220 | 4.75
346 | 8 | 1.2699 | 0.45118 | 35.5291 | 1.53 | 220 | 4.86
431 | 1.6 | 1.2699 | 0.1124 | 8.8515 | 1.53 | 220 | 4.84
※ PERFOR MANCE CURVE
PASS-931SS-T