## 펌프외형도
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 최대양수량 (ℓ/h) | 31800 | 모 터 부 | 정 격 출 력 (㎾) | 1.5
| 흡 상 고 (m) | 0 |  | 정 격 전 압 (V) | 220/380
| 압 상 고 (m) | 30 |  | 정 격 주 파 수 (Hz) | 60
| 흡 입 경 (A) | 50A |  | 회 전 수 (rpm) | 3400
| 토 출 경 (A) | 50A |  | 모 터 Type | 단상 2극
(단위 : mm)
|  |  | PUMP Type |  | 볼류트형
|  |  | 형 식 |  | PASS-1681SS-T

## 펌프단면도
펌 프 단 면 도
NO | 부 품 명 | 재 질 | NO | 부 품 명 | 재 질
1 | 모타홴커버 | SPCC | 13 | 베드 | SCP-1
2 | 모터휀 | NYLON66+GF25% | 14 | 미케니컬시일 | 18
3 | 모타샤프트 | SM20C+STS316 | 15 | 베어링(부하) | 6205ZZ
4 | 모터커버 | GC-200 | 16 | 베어링 캡 | SECC
5 | 모터프래임 | AL 6033-T5 | 17 | 모터프레임받침고무 | NBR60°
6 | 콘덴서커버 | PP | 18 | 베어링(반부하) | 6204ZZ
7 | - | - | 19 | 유동스프링 | 6204
8 | 로터DC | 전기강판+ALDC | 20
9 | 스테타조립 | - | 21
10 | 홀더 | SSC13 | 22
11 | 케이싱 | SSC13 | 23
12 | 임펠러 | SSC13 | 24
|  |  | PUMP Type |  | 볼류트형
|  |  | 형 식 |  | PASS-1681SS-T

## data sheet
PUMP DATA SHEET
Model | PASS-1681SS-T | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■ In, □ out
OPERATING CONDITION
Liquid | Water | Flow | 290 ℓ/min at Ht=19m
Pumping Temp | 0℃ ~ 40℃ | Suct. Head | 0m
Specific Gravity |  | Disch. Head | 30m
Vapor Pressure | ㎏/㎠A | Total Head | 30m
Viscosity | cP
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
■ Horizontal □ Vertical |  | Efficiency |  |  | (Parts' Name)
Number of Stages | Stage | Rated Power | 1500 W |  | Impeller | SSC13
Speed | 3400rpm | NPSHre | mAq |  | frame | AL 6033-T5
Rotation | □ CW, ■ CCW (viewed from pump head) |  |  |  | Shaft | SM20C+STS316
Flange | Size(Dia) | Rating | Face | Position | Casing | SSC13
Suction | 50A |  | ■ FF, □ RF | □TOP ■Side | Suct. Flange | -
Discharge | 50A |  | ■ FF, □ RF | ■TOP □Side | Disch. Flange | -
Impeller Type | volute type | ■ Single Suct □ Double Suct |  | HYDROSTATIC | motor cover | GC-200
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | 5 ㎏/㎠ | 3 Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Pressure Tank | ㎏/㎠ | Min
Shaft Sleeve | □ Yes ■ No
Mounting | ■ Foot □ Centerline |  |  | TESTING
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) | (self test) | (Witness)
Cooling | □ Stuff. Box □ B/R Housing ■ Fan Cooling |  |  | Run Perform | ■ Yes □ No | □ Yes ■No
R Bearing | 6204 zz | F Bearing | 6205 zz | Hydrostatic | ■ Yes □ No | □ Yes ■No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220/380 | 1 | 60 | Impeller
Maker | HANIL PUMP LTD,. |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 1500W |  |  |  | Casing Ring
Pole&Speed | 2P 3400rpm | Insulation Class | ■ F □ E |  | Bearing(R+F)
ACCESSORIES |  |  |  |  | M/Seal
■ Base Plate | □ Cast Iron □ Plastic ■ Steel Plate |  |  |  | Oil Seal
□ Unions
□ Coupling | □ Sun Flex □ Wood □ Grid ■ No |  |  |  | Coupling
□ Pressure Gauge | □ Suct. Vacuum □ Suct. Compound □ Disch. Press ■ No |  |  |  | Coupling Rubber
■ Plug for priming & Screw for Drain |  |  |  |  | Name Plate
Mechnical Seal | Maker | EKK | Model & Size | φ18 | WEIGHT
| Type | HK9A-LN18 | Cooler | □ Yes ■ No | Pump/Bed | Kg
□ Companion Flange |  |  |  |  | Driver | Kg
□ Special Tools |  |  |  |  | Total Wt.(net) | 31 Kg

## test report
PUMP TEST REPORT
※SPELIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(ℓ/min) | 290 |  | Phase(φ) |  | 1 | Out Put | 1.5 (㎾)
Head(m) | 19 |  | Pole(p) |  | 2 | Freq | 60 (Hz)
suct,disch(A) | 50A |  | Volt(v) |  | 220/380 | Maker | HANIL
Model | PASS-1681SS-T |  | Customer
※ PERFOR MANCE DATA (Test by Ks B 6301)
Capacity(ℓ/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | In put(kw) | Vol tage(V) | Current(A)
0 | 32 | 0.98604 | 0 | 0 | 1.188 | 380 | 2.89
272 | 21 | 1.8434 | 0.93106 | 50.5067 | 2.221 | 380 | 4.15
368 | 16 | 1.9231 | 0.95974 | 49.9058 | 2.317 | 380 | 4.28
479 | 10 | 1.9995 | 0.78077 | 39.0488 | 2.409 | 380 | 4.43
533 | 4.4 | 1.9854 | 0.38227 | 19.2543 | 2.392 | 380 | 4.4
※ PERFOR MANCE CURVE
PA-1688SS