## 펌프외형도
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 정 격 양 수 량 |  | 100ℓ/min(22m시) |  | 가압펌프 | 모 터 부 | 정 격 출 력 (㎾) |  | 0.9
| 흡 상 고 (m) |  | 0 |  |  |  | 정 격 전 압 (V) |  | 220
| 압 상 고 (m) |  | 28 |  |  |  | 정 격 주 파 수 (Hz) |  | 60
| 흡 입 경 (mm) |  | 32A |  |  |  | 회 전 수 (rpm) |  | 3400
| 토 출 경 (mm) |  | 25A |  |  |  | 모 터 Type |  | 단상 2극
각 부 치 수(mm)
A |  | B |  | C |  | D |  | E |  | F
210 |  | 260 |  | 135 |  | 52 |  | 325 |  | 330
[7 empty] | PUMP TYPE |  | 가압펌프
[7 empty] | 형 식 |  | PSS 120-096

## 펌프단면도
펌 프 단 면 도
NO | 부 품 명 | 재 질 | NO | 부 품 명 | 재 질
1 | 모터홴커버 | SPCC 1.0t | 16 | 임펠러조립 | STS-304
2 | 모터홴 | PP(J-350) | 17 | 케이싱 | STS-304 1.5t
3 | 모터커버 | ALDC | 18 | 케이싱보강판 | STS-304 1.5t
4 | 베어링 | 6203zz | 19 | 흡입관 (1 1/4") | STS-304
5 | 콘덴서커버 | PP(J-350) | 20 | 캡너트 | STS-304
6 | 스테이터조립 | HL CORE 70mm(규소) | 21 | 키 | STS-304
7 | 로터DC | 홴일체형 70mm(규소) | 22 | 물빼기캡 | 황동(크롬도금)
8 | 콘덴서 | 450V 20㎌ | 23 | 물빼기캡패킹 | NBR
9 | 모터샤프트 | SM20C+STS316 | 24 | 베 드 | SPCC 2.0t
10 | 장볼트 | MSWR | 25 | 미캐니컬실 | STS-316
11 | 코드붓싱 | NBR | 26 | 육각렌치볼트 | STS M6×15L
12 | 베어링 | 6204 zz | 27 | 케이싱 패킹 | NBR
13 | 홀더 | ALDC | 28 | 육각볼트 | STS-304
14 | 케이싱 부착판 | STS-304 1.5t | 29 | 멈춤링 | 20호
15 | 토출관 (1") | STS-304 | 30 | 유동스프링 | BWW-6203
|  |  | PUMP Type |  | 가압펌프
|  |  | 형 식 |  | PSS 120-096

## data sheet
PUMP DATA SHEET
Model | PSS 120-096 | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■ In, □ out
OPERATING CONDITION
Liquid | Water | Flow | 100 ℓ/min at Ht=22m
Pumping Temp | 0℃ ~ 40℃ | Suct. Head | 0m
Specific Gravity |  | Disch. Head | 28m
Vapor Pressure | ㎏/㎠A | Total Head | 28m
Viscosity | cP
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
■ Horizontal □ Vertical |  | Efficiency |  |  | (Parts' Name) | Symbol㉿
Number of Stages | Stage | Rated Power |  |  | Impeller | STS - 304
Speed | 3400 rpm | NPSHre | mAq |  | Impeller cover | -
Rotation | □ CW, ■ CCW (viewed from pump head) |  |  |  | Shaft | STS - 316
Flange | Size(Dia) | Rating | Face | Position | Casing | STS - 304
Suction | 32A |  | □ FF, □ RF | □TOP ■Side | Suct. Flange | -
Discharge | 25A |  | □ FF, □ RF | ■TOP □Side | Disch. Flange | -
Impeller Type | close Type | ■ Single Suct □ Double Suct |  | HYDROSTATIC | Guide Vane | -
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | 10 ㎏/㎠ | 1 Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Pressure Tank | 10 ㎏/㎠ | 1 Min
Shaft Sleeve | □ Yes ■ No
Mounting | ■ Foot □ Centerline |  |  | TESTING
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) | (self test) | (Witness)
Cooling | □ Stuff. Box □ B/R Housing ■ Fan Cooling |  |  | Run Perform | ■ Yes □ No | □ Yes □ No
R Bearing | 6203 zz | F Bearing | 6204 zz | Hydrostatic | ■ Yes □ No | □ Yes □ No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller
Maker | HANIL PUMP Co., Ltd. |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 0.9 kW |  |  |  | Casing Ring
Pole&Speed | 2P 3400rpm | Insulation Class | □ F ■ E |  | Bearing(R+F)
ACCESSORIES |  |  |  |  | M/Seal
■ Base Plate | □ Cast Iron □ Plastic ■ Steel Plate |  |  |  | Oil Seal
□ Unions
□ Coupling | □ Sun Flex □ Wood □ Grid ■ No |  |  |  | Coupling
□ Pressure Gauge | □ Suct. Vacuum □ Suct. Compound □ Disch. Press ■ No |  |  |  | Coupling Rubber
■ Plug for priming & Screw for Drain |  |  |  |  | Name Plate
Mechnical Seal | Maker | EAGLE | Model & Size | φ14 | WEIGHT
| Type | EA103-014SH | Cooler | □ Yes ■ No | Pump/Bed | Kg
□ Companoion Flange |  |  |  |  | Driver | Kg
□ Special Tools |  |  |  |  | Total Wt.(net) | 16.7 Kg

## test report
PUMP TEST REPORT
※SPELIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(ℓ/min) | 100 |  | Phase(φ) |  | 1 | Out Put | 0.9kW
Head(m) | 22 |  | Pole(p) |  | 2 | Freq | 60 (Hz)
suct,disch(mm) | 32A, 25A |  | Volt(v) |  | 220 | Maker | HANIL
Model | PSS 120-096 |  | Customer
※ PERFOR MANCE DATA (Test by Ks B 6301)
Capacity(ℓ/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | out put(kw) | Vol tage(V) | Current(A)
0 | 37.5 | 0.7119 | 0 | 0 | 1.13 | 220 | 5.35
70 | 30 | 0.93681 | 0.3423 | 36.5389 | 1.487 | 220 | 7.08
98.6 | 26 | 1.0099 | 0.41787 | 41.3775 | 1.603 | 220 | 7.66
150 | 15 | 1.0849 | 0.36675 | 33.8062 | 1.722 | 220 | 8.27
181 | 5 | 0.99729 | 0.14752 | 14.7916 | 1.583 | 220 | 7.55
187.4 | 2.2 | 0.9702 | 0.067202 | 6.9266 | 1.54 | 220 | 7.28
※ PERFOR MANCE CURVE