## 펌프외형도
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 최대양수량 (ℓ/h) | 8400 | 모 터 부 | 정 격 출 력 (㎾) | 0.9
| 흡 상 고 (m) | 0 |  | 정 격 전 압 (V) | 220
| 압 상 고 (m) | 25 |  | 정 격 주 파 수 (Hz) | 60
| 흡 입,토출경 (mm) | 32 / 25 |  | 회 전 수 (rpm) | 3400
| 압력스위치 (㎏/㎠) | 2.5~3.3 |  | 모 터 Type | 단상 2극
(단위 : mm)
|  |  | PUMP Type |  | 가압용펌프
|  |  | 형 식 |  | PSS 80-096KV

## 펌프단면도
펌 프 단 면 도
NO | 부 품 명 | 재 질 | NO | 부 품 명 | 재 질
1 | 모터홴커버 | SPCC 1.0t | 14 | 체크밸브 | 25A
2 | 베어링 | 6203zz | 15 | 플렉시블호스 | -
3 | 모터홴 | PP(J-350) | 16 | 케이싱조립 | STS
4 | 모터커버 | ALDC | 17 | 에어및물빼기나사 | 황동(크롬도금)
5 | 콘덴서 및 커버 | 450V 20㎌ | 18 | 흡입구 유니온 | 32A
6 | 장 볼 트 | STS-304 | 19 | 임펠러조립 | STS
7 | 스테이터조립 | 적고90mm | 20 | 질소탱크 | 60L
8 | 로터조립 | 적고90mm | 21 | 미케니컬실 | STS-316
9 | 베어링 | 6204zz | 22 | 케이싱볼트 | STS
10 | 케이싱보강판 | sts-304 | 23 | 홀 더 | ALDC
11 | 압력스위치 | PM-5 | 24 | 베 드 | SPCC
12 | 압력계 | - | 25 | 모터사프트 | SM20C+STS316
13 | 토출밸브 | 25A | 26 | 유동스프링 | BWW-6203
|  |  | PUMP Type |  | 가압용펌프
|  |  | 형 식 |  | PSS 80-096KV

## data sheet
PUMP DATA SHEET
Model | PSS 80-096KV | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■ In, □ out
OPERATING CONDITION
Liquid | Water | Flow | 55 ℓ/min at Ht=28m
Pumping Temp | 0℃ ~ 40℃ | Suct. Head | 0m
Specific Gravity | 1 | Disch. Head | 25m
Vapor Pressure | ㎏/㎠A | Total Head | 25m
Viscosity | cP |  |  |  | Pressure s/w | 2.5~3.3 ㎏/㎠
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
■ Horizontal □ Vertical |  | Efficiency |  |  | (Parts' Name) | Symbol㉿
Number of Stages | Stage | Rated Power | 0.9 kW |  | Impeller | STS-304
Speed |  | NPSHre | mAq |  | Impeller cover | -
Rotation | □ CW, ■ CCW (viewed from pump head) |  |  |  | Shaft | SM20C+STS303
Flange | Size(Dia) | Rating | Face | Position | Casing | STS-304
Suction | 32㎜ |  | □ FF, ■ RF | □TOP ■Side | Suct. Flange | -
Discharge | 25㎜ |  | □ FF, ■ RF | ■TOP □Side | Disch. Flange | -
Impeller Type | Close Type | ■ Single Suct □ Double Suct |  | HYDROSTATIC | Guide Vane | -
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | 10 ㎏/㎠ | 1 Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Pressure Tank | ㎏/㎠ | Min
Shaft Sleeve | □ Yes ■ No
Mounting | □ Foot □ Centerline |  |  | TESTING
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) | (self test) | (Witness)
Cooling | □ Stuff. Box □ B/R Housing ■ Fan Cooling |  |  | Run Perform | ■ Yes □ No | □ Yes □ No
R Bearing | 6204 zz | F Bearing | 6203 zz | Hydrostatic | ■ Yes □ No | □ Yes □ No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller
Maker | HANIL PUMP LTD,. |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 0.9 kW |  |  |  | Casing Ring
Pole&Speed | 2P 3400rpm | Insulation Class | ■ E □ B |  | Bearing(R+F)
ACCESSORIES |  |  |  |  | M/Seal
□ Base Plate | □ Cast Iron □ Plastic □ Steel Plate |  |  |  | Oil Seal
□ Unions
□ Coupling | □ Sun Flex □ Wood □ Grid ■ No |  |  |  | Coupling
□ Pressure Gauge | □ Suct. Vacuum □ Suct. Compound □ Disch. Press ■ No |  |  |  | Coupling Rubber
■ Plug for priming & Screw for Drain |  |  |  |  | Name Plate
Mechnical Seal | Maker | EKK | Model & Size | φ14 | WEIGHT
| Type | EA103-014SH | Cooler | □ Yes ■ No | Pump/Bed | Kg
□ Companoion Flange |  |  |  |  | Driver | Kg
□ Special Tools |  |  |  |  | Total Wt.(net) | 36 Kg

## test report
PUMP TEST REPORT
※SPELIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(ℓ/min) | 140 |  | Phase(φ) |  | 1 | Out Put | 0.9(㎾)
Head(m) | 25 |  | Pole(p) |  | 2 | Freq | 60 (Hz)
suct,disch(mm) | 32 / 25 |  | Volt(v) |  | 220 | Maker | HANIL
Model | PSS 80-096KV |  | Customer
※ PERFOR MANCE DATA (Test by Ks B 6301)
Capacity(ℓ/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | In put(kw) | Vol tage(V) | Current(A)
0 | 38.7 | 0.6048 | 0 | 0 | 0.96 | 220 | 4.39
32.3 | 34 | 0.7434 | 0.17901 | 24.0794 | 1.18 | 220 | 5.4
58 | 30 | 0.83727 | 0.28362 | 33.8744 | 1.329 | 220 | 6.09
82.1 | 25 | 0.92358 | 0.33456 | 36.224 | 1.466 | 220 | 6.7
120.7 | 15 | 1.0111 | 0.29511 | 5 | 1.605 | 220 | 7.37
150.6 | 1.8 | 1.0313 | 0.044186 | 4.2845 | 1.637 | 220 | 7.54
※ PERFOR MANCE CURVE