## 펌프외형도
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 최대양수량 (ℓ/h) | 22200 | 모 터 부 | 정 격 출 력 (㎾) | 5.5
| 흡 상 고 (m) | 0 |  | 정 격 전 압 (V) | 220/380
| 압 상 고 (m) | 110 |  | 정 격 주 파 수 (Hz) | 60
| 흡 입 경 (mm) | 50 |  | 회 전 수 (rpm) | 3400
| 토 출 경 (mm) | 50 |  | 모 터 Type | 삼상 2극
(단위 : mm)
|  |  | PUMP Type |  | 부스터 펌프
|  |  | 형 식 |  | HHP-5607B-T

## 펌프단면도
펌 프 단 면 도
..
NO | 부 품 명 | 재 질 | NO | 부 품 명 | 재 질
1 | 모터ASS'Y | - | 14 | 육각볼트 | SS41
2 | 연결플랜지 | GC-200 | 15 | 로그너트 | MBSBD
3 | 흡입구케이싱 | BC 6 | 16 | 가이드베인 본체 | STS-304
4 | 메카니컬 씰 | ceramics+carbon | 17 | 가이드베인 | NORYL+GF30%
5 | 연결커플링부싱 | STS-304 | 18 | 임펠러 조립 | NORYL+GF30%
6 | 연결커플링 | STS-304 | 19 | 스러스트와셔 | STS-304
7 | 커플링고정나사 | SCM | 20 | 오링 | NBR
8 | 와셔 | SS41 | 21 | 플러그 | MBSBD
9 | 모터샤프트 | STS-304 | 22 | 수절고무 | NBR
10 | 펌프케이스 | STS-304 | 23 | 육각볼트 | SS41
11 | 수평받침대 | GC-200 | 24 | 육각볼트 | SS41
12 | 토출구하우징 | BC 6 | 25 | 베 드 | SPCC
13 | 송수고무부싱 | NBR | 26
|  |  | PUMP Type |  | 부스터 펌프
|  |  | 형 식 |  | HHP-5607B-T

## data sheet
PUMP DATA SHEET
Model | HHP-5607B-T | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■ In, □ out
OPERATING CONDITION
Liquid | Water | Flow | 370 ℓ/min at Ht=0.5m
Pumping Temp | 0℃ ~ 60℃ | Suct. Head | 0m
Specific Gravity |  | Disch. Head | 110m
Vapor Pressure | ㎏/㎠A | Total Head | 110m
Viscosity | cP
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
■ Horizontal □ Vertical |  | Efficiency |  |  | (Parts' Name)
Number of Stages | Stage | Rated Power | 5.5kW |  | Impeller | NORYL+GF30%
Speed | 3400rpm | NPSHre | mAq |  | frame | GC-200
Rotation | ■ CW, □ CCW (viewed from motor fan cover) |  |  |  | Shaft | STS-304
Flange | Size(Dia) | Rating | Face | Position | Casing | GC-200
Suction | 50㎜ |  | ■ FF, □ RF | □TOP ■Side | Suct. Flange | -
Discharge | 50㎜ |  | ■ FF, □ RF | □TOP ■Side | Disch. Flange | -
Impeller Type | BOOSTER | ■ Single Suct □ Double Suct |  | HYDROSTATIC | motor cover | GC-200
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | 12㎏/㎠ | 3 Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Pressure Tank | ㎏/㎠ | Min
Shaft Sleeve | □ Yes ■ No
Mounting | ■ Foot □ Centerline |  |  | TESTING
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) | (self test) | (Witness)
Cooling | □ Stuff. Box □ B/R Housing ■ Fan Cooling |  |  | Run Perform | ■ Yes □ No | □ Yes ■No
R Bearing | 6306 zz | F Bearing | 6308 zz | Hydrostatic | ■ Yes □ No | □ Yes ■No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220/380 | 3 | 60 | Impeller
Maker | HANIL PUMP LTD,. |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 5.5kW |  |  |  | Casing Ring
Pole&Speed | 2P 3400rpm | Insulation Class | □ E ■ B |  | Bearing(R+F)
ACCESSORIES |  |  |  |  | M/Seal
■ Base Plate | □ Cast Iron □ Plastic ■ Steel Plate |  |  |  | Oil Seal
□ Unions
□ Coupling | □ Sun Flex □ Wood □ Grid □ No |  |  |  | Coupling
□ Pressure Gauge | □ Suct. Vacuum □ Suct. Compound □ Disch. Press ■ No |  |  |  | Coupling Rubber
■ Plug for priming & Screw for Drain |  |  |  |  | Name Plate
Mechnical Seal | Maker | EKK | Model & Size | φ32 | WEIGHT
| Type | EA103-32 | Cooler | □ Yes ■ No | Pump/Bed | Kg
□ Companion Flange |  |  |  |  | Driver | Kg
□ Special Tools |  |  |  |  | Total Wt.(net) | 91 Kg

## test report
PUMP TEST REPORT
※SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(ℓ/min) | 370 |  | Phase(φ) |  | 3 | Out Put | 5.5(㎾)
Total Head(m) | 110 |  | Pole(p) |  | 2 | Freq | 60 (Hz)
suct,disch(mm) | 50, 50 |  | Volt(v) |  | 220/380 | Maker | HANIL
Model | HHP-5607B-T |  | Customer
※ PERFORMANCE DATA (Test by Ks B 6301)
Capacity(ℓ/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | Input(kw) | Voltage(V) | Current(A)
0 | 119 | 2.9925 | 0 | 0 | 3.99 | 380 | 6.9
159 | 100 | 4.8375 | 2.5917 | 53.5752 | 6.45 | 380 | 10.8
228 | 80 | 5.2575 | 2.9731 | 56.5501 | 7.01 | 380 | 11.6
278 | 60 | 5.2575 | 2.7188 | 51.7136 | 7.01 | 380 | 11.6
320 | 40 | 5.16 | 2.0864 | 40.4341 | 6.88 | 380 | 11.5
358 | 20 | 5.1825 | 1.1671 | 22.5196 | 6.91 | 380 | 11.5
※ PERFORMANCE CURVE