## 펌프외형도
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 정 격 양 수 량 |  | 38ℓ/min(60m시) |  | 가압펌프 | 모 터 부 | 정 격 출 력 (㎾) | 1.5
| 흡 상 고 (m) |  | 0 |  |  |  | 정 격 전 압 (V) | 220
| 압 상 고 (m) |  | 85 |  |  |  | 정 격 주 파 수 (Hz) | 60
| 흡 입 경 (mm) |  | 25A |  |  |  | 회 전 수 (rpm) | 3400
| 토 출 경 (mm) |  | 25A |  |  |  | 모 터 Type | 단상 2극
각 부 치 수(mm)
A |  | B |  | C |  | D
483 |  | 260 |  | 113 |  | 200
[7 empty] | PUMP TYPE | 횡형 다단펌프
[7 empty] | 형 식 | HHPS-2602

## 펌프단면도
펌 프 단 면 도
*대표기종 HHPS-3402-T
| NO | 부 품 명 | 재 질 | NO | 부 품 명 | 재 질
| 1 | 흡입구 케이싱 | SSC-13(STS-304) | 16 | 장볼트 | SM45C ZPC
| 2 | 볼트,와셔 | STS-304 | 17 | 베어링 | 6204zz
| 3 | 에어벤트 | 황동 | 18 | 모터커버 | GC-150
| 4 | 임펠러조립 | STS-304 | 19 | 웨이브와셔 | #6303
| 5 | 가이드베인하조립 |  | 20 | 모터홴조립 | PA-66+SPCC
| 6 | 임펠러하우징 |  | 21 | 모터홴 커버 | SPCC
| 7 | 패킹 | 아스베스토 | 22 | 베드
| 8 | 가이드베인조립 | STS-304 | 23 | 모터프레임 받침고무 | NBR
| 9 | 토출구 케이싱 | SSC-13(STS-304) | 24 | C형 멈춤링 | SPS HRC44-52 ACP
| 10 | 미케니컬 씰 | STS-316 | 25 | 스톱링 | STS-304
| 11 | 모터샤프트 | SM20C+STS-303 | 26 | 스톱퍼
| 12 | 베어링 | 6205 zz | 27 | 스러스트부싱E
| 13 | 단자커버 | ALDC | 28 | 스러스트부싱G
| 14 | 스테이터조립 | S-18 | 29 | 스러스트부싱F
| 15 | 로터 DC | S-18+ALDC | 30 | 육각렌치 볼트 | SCM+크롬도금
|  |  |  | 31 | 물빼기 캡 | 황동
|  |  |  | PUMP Type |  | 가압펌프
|  |  |  | 형 식 |  | HHPS-2602

## data sheet
PUMP DATA SHEET
Model | HHPS-2602 | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■ In, □ out
OPERATING CONDITION
Liquid | Water | Flow | 38 ℓ/min at Ht=60m
Pumping Temp | 0℃ ~ 80℃ | Suct. Head | 0m
Specific Gravity |  | Disch. Head | 85m
Vapor Pressure | ㎏/㎠A | Total Head | 85m
Viscosity | cP
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
■ Horizontal □ Vertical |  | Efficiency |  |  | (Parts' Name) | Symbol㉿
Number of Stages | Stage | Rated Power |  |  | Impeller | STS - 304
Speed | 3400 rpm | NPSHre | mAq |  | Impeller cover | -
Rotation | □ CW, ■ CCW (viewed from pump head) |  |  |  | Shaft | STS - 303
Flange | Size(Dia) | Rating | Face | Position | Casing | STS - 304
Suction | 25A |  | □ FF, □ RF | □TOP ■Side | Suct. Flange | -
Discharge | 25A |  | □ FF, □ RF | ■TOP □Side | Disch. Flange | -
Impeller Type | close Type | ■ Single Suct □ Double Suct |  | HYDROSTATIC | Guide Vane | -
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | 10 ㎏/㎠ | 1 Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Pressure Tank | 10 ㎏/㎠ | 1 Min
Shaft Sleeve | □ Yes ■ No
Mounting | ■ Foot □ Centerline |  |  | TESTING
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) | (self test) | (Witness)
Cooling | □ Stuff. Box □ B/R Housing ■ Fan Cooling |  |  | Run Perform | ■ Yes □ No | □ Yes □ No
R Bearing | 6205 zz | F Bearing | 6204 zz | Hydrostatic | ■ Yes □ No | □ Yes □ No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller
Maker | HANIL PUMP Co., Ltd. |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 1.5 kW |  |  |  | Casing Ring
Pole&Speed | 2P 3400rpm | Insulation Class | ■ F □ E |  | Bearing(R+F)
ACCESSORIES |  |  |  |  | M/Seal
■ Base Plate | □ Cast Iron □ Plastic ■ Steel Plate |  |  |  | Oil Seal
□ Unions
□ Coupling | □ Sun Flex □ Wood □ Grid ■ No |  |  |  | Coupling
□ Pressure Gauge | □ Suct. Vacuum □ Suct. Compound □ Disch. Press ■ No |  |  |  | Coupling Rubber
■ Plug for priming & Screw for Drain |  |  |  |  | Name Plate
Mechnical Seal | Maker | EAGLE | Model & Size | φ12 | WEIGHT
| Type | EE220-012 | Cooler | □ Yes ■ No | Pump/Bed | kg
□ Companoion Flange |  |  |  |  | Driver | kg
□ Special Tools |  |  |  |  | Total Wt.(net) | 26 kg

## test report
PUMP TEST REPORT
※SPELIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(ℓ/min) | 38 |  | Phase(φ) |  | 1 | Out Put
Head(m) | 60 |  | Pole(p) |  | 2 | Freq | 60 (Hz)
suct,disch(mm) | 25A |  | Volt(v) |  | 220 | Maker | HANIL
Model | HHPS-2602 |  | Customer
※ PERFOR MANCE DATA (Test by Ks B 6301)
Capacity(ℓ/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | out put(kw) | Vol tage(V) | Current(A)
0 | 90.9 | 1.0947 | 0 | 0 | 1.45 | 220 | 6.7
29.5 | 70 | 1.4043 | 0.3366 | 23.9689 | 1.86 | 220 | 8.42
40.9 | 60 | 1.4345 | 0.4 | 27.8844 | 1.9 | 220 | 8.9
60.4 | 40 | 1.5704 | 0.39381 | 25.0769 | 2.08 | 220 | 9.36
77.8 | 20 | 1.5628 | 0.25363 | 16.2286 | 2.07 | 220 | 9.48
86 | 10 | 1.51 | 0.14018 | 9.2834 | 2 | 220 | 9.22
※ PERFOR MANCE CURVE