## 펌프외형도
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 정 격 양 수 량 | 100 | 170 | BOOSTER | 모 터 부 | 정 격 출 력 (㎾) | 1.5
| 흡 상 고 (m) | 0 |  |  |  | 정 격 전 압 (V) | 220/380
| 압 상 고 (m) | 30 | 25 |  |  | 정 격 주 파 수 (Hz) | 60
| 흡 입 경 (m) | 40 |  |  |  | 회 전 수 (rpm) | 3400
| 토 출 경 (m) | 25 |  |  |  | 모 터 Type | 삼상 2극
각 부 치 수(mm)
| A | B |  | C |  | D
| 350 | 260 |  | 208 |  | 106
[6 empty] | PUMP TYPE | 스테인리스 펌프
[6 empty] | 형 식 | HE-CDX 200/206T

## data sheet
PUMP DATA SHEET
Model | HEIG-50LPD61.5-3T | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■ In, □ out
OPERATING CONDITION
Liquid | Water | Flow
Pumping Temp | 0℃ ~ 100℃ | Suct. Head
Specific Gravity |  | Disch. Head
Vapor Pressure | ㎏/㎠A | Total Head
Viscosity | cP
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
■ Horizontal □ Vertical |  | Efficiency |  |  | (Parts' Name) | Symbol㉿
Number of Stages | Stage | Rated Power |  |  | Impeller | STS - 304
Speed | 3400 rpm | NPSHre | mAq |  | Impeller cover | -
Rotation | □ CW, ■ CCW (viewed from pump head) |  |  |  | Shaft | STS - 304
Flange | Size(Dia) | Rating | Face | Position | Casing | STS - 304
Suction | 40㎜ |  | □ FF, □ RF | □TOP ■Side | Suct. Flange | -
Discharge | 25㎜ |  | □ FF, □ RF | ■TOP □Side | Disch. Flange | -
Impeller Type | close Type | ■ Single Suct □ Double Suct |  | HYDROSTATIC | Guide Vane
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | 10 ㎏/㎠ | 1 Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Pressure Tank | 10 ㎏/㎠ | 1 Min
Shaft Sleeve | □ Yes ■ No
Mounting | ■ Foot □ Centerline |  |  | TESTING
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) | (self test) | (Witness)
Cooling | □ Stuff. Box □ B/R Housing ■ Fan Cooling |  |  | Run Perform | ■ Yes □ No | □ Yes □ No
R Bearing | 6203zz c3 | F Bearing | 6202 zz c3 | Hydrostatic | ■ Yes □ No | □ Yes □ No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220/380 | 3 | 60 | Impeller
Maker | EBARA |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 1.5 kW |  |  |  | Casing Ring
Pole&Speed | 2P 3400rpm | Insulation Class | ■ E □ B |  | Bearing(R+F)
ACCESSORIES |  |  |  |  | M/Seal
□ Base Plate | □ Cast Iron □ Plastic □ Steel Plate |  |  |  | Oil Seal
□ Unions
□ Coupling | □ Sun Flex □ Wood □ Grid □ No |  |  |  | Coupling
□ Pressure Gauge | □ Suct. Vacuum □ Suct. Compound □ Disch. Press ■ No |  |  |  | Coupling Rubber
■ Plug for priming & Screw for Drain |  |  |  |  | Name Plate
Mechnical Seal | Maker |  | Model & Size |  | WEIGHT
| Type |  | Cooler | □ Yes ■ No | Pump/Bed | Kg
□ Companoion Flange |  |  |  |  | Driver | Kg
□ Special Tools |  |  |  |  | Total Wt.(net) | 18 Kg

## test report
PUMP TEST REPORT
※SPELIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(ℓ/min) |  |  | Phase(φ) |  | 3 | Out Put | 1.5 (㎾)
Head(m) |  |  | Pole(p) |  | 2 | Freq | 60 (Hz)
suct,disch(mm) | 32A-25A |  | Volt(v) |  | 220V/380V | Maker | EBARA
Model | HEIG-50LPD61.5-3T |  | Customer
※ PERFOR MANCE DATA (Test by Ks B 6301)
Capacity(ℓ/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | out put(kw) | Vol tage(V) | Current(A)
0 | 33 | 0.7482 | 0 | 0 | 0.86 | 220 | 1.83
100 | 30 | 1.1493 | 0.489 | 42.5487 | 1.321 | 220 | 2.41
169 | 25 | 1.4694 | 0.68868 | 46.8668 | 1.689 | 220 | 2.92
235 | 20 | 1.6634 | 0.7661 | 46.0552 | 1.912 | 220 | 3.26
279 | 15 | 1.7974 | 0.68215 | 37.9519 | 2.066 | 220 | 3.49
320 | 8 | 1.8131 | 0.41728 | 23.015 | 2.084 | 220 | 3.52
※ PERFOR MANCE CURVE