## 펌프외형도
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 양수량 (L/min) | 430 (25m) | 모 터 부 | 정 격 출 력 (㎾) | 3.75
| 흡 상 고 (m) | 0 |  | 정 격 전 압 (V) | 220/380
| 압 상 고 (m) | 34 |  | 정 격 주 파 수 (Hz) | 60
| 흡 입 경 (mm) | 65A |  | 회 전 수 (rpm) | 3400
| 토 출 경 (mm) | 40A |  | 모 터 Type | 삼상 2극
(단위 : mm)
|  |  | PUMP Type |  | CENTRIFUGAL PUMP
|  |  | 형 식 |  | HE-3SF-40-125/3.06

## 펌프단면도
펌 프 단 면 도
NO | 부 품 명 | 재 질 | NO | 부 품 명 | 재 질
1 | 케이싱 | STS-304 | 25 | 물빼기나사 | STS-304
3 | 홀더 브라켓 | GC-200 | 32 | 키 | STS-304
6 | 커플러 | STS-304 | 34 | 임펠러 고정너트 | STS-304
7 | 임펠러 | STS-304 | 42 | 베드 | SECC
11 | 미케니컬실 | Carbom/Ceramic/NBR | 44 | 보호판 | STS-304
12 | 모터프레임조립 | ALDC
|  |  | PUMP Type |  | CENTRIFUGAL PUMP
|  |  | 형 식 |  | HE-3SF-40-125/3.06

## data sheet
PUMP DATA SHEET
Model | HE-3SF-40-125/3.06 |  |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■ In □out
OPERATING CONDITION
Liquid | Water | Flow | 430 L/min at Ht=25 m |  | NPSHav | mAq
Pumping Temp | 0℃ ~ 80℃ | Suct. Head | 0 m |  | Concentration | %
Sp. Gr. @P. T |  | Disch. Head | 34 m |  | Solid
Vap.Press @P.T | ㎏/㎠A | Total Head | 34 m |  | Corros. or Erros
Visc @P. T | 1 Cp
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
■ Horizontal □ Vertical |  | Efficiency |  |  | (Parts' Name)
Number of Stages | 1 Stage | Rated Power | 3.75 kW |  | Impeller | STS304
Speed |  | NPSHre |  |  | Shaft | SM20C+STS-304
Rotation | □ CW, ■ CCW (viewed from Casing) |  |  |  | Casing | STS304
Flange | Size(Dia) | Rating | Face | Position | Suct. Flange | -
Suction | 65A |  | ■ FF, □ RF | □TOP ■Side | Disch. Flange | -
Discharge | 40A |  | ■ FF, □ RF | ■TOP □Side
Impeller Type | CLOSED Type | ■ Single Suct □ Double Suct |  | HYDROSTATIC
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | 3.4 ㎏/㎠ | 3 Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Pressure Tank | ㎏/㎠ | Min
Shaft Sleeve | □ Yes ■ No
Mounting | □ Foot □ Centerline |  |  | TESTING
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) | (self test) | (Witness)
Cooling | □ Stuff. Box □ B/R Housing □ Fan Cooling |  |  | Run Perform | ■ Yes □ No | □ Yes ■ No
Radial Bearing | - | Thrust Bearing | - | Hydrostatic | ■ Yes □ No | □ Yes ■ No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220/380 | 3 | 60 | Impeller
Maker | HANIL PUMP |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 3.75 kW |  |  |  | Casing Ring
Pole&Speed | 2P / 3,350rpm | Insulation Class | ■F □ E □ B |  | Bearing(R+T)
ACCESSORIES |  |  |  |  | M/Seal
□ Base Plate | □ Cast Iron □ Plastic □ Steel Plate |  |  | □ Drain Rim | Oil Seal
Coupling | □ Sun Flex □ Wood □ Grid ■ No |  |  |  | Coupling
Press Gauge | □ Suct. Vacuum □ Suct. Compound □ Disch. Press ■ No |  |  |  | Coupling Rubber
□ Plug for priming & Screw for Drain |  |  |  |  | Name Plate
Mechnical Seal | Maker | EAGLE | Model & Size |  | WEIGHT
| Type |  | Cooler | □ Yes ■ No | Pump/Bed | Kg
□ Companoion Flange |  |  |  |  | Driver | Kg
□ Special Tools |  |  |  |  | Total Wt | 57 Kg

## test report
PUMP TEST REPORT
※SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(L/min) | 430 (25m) |  | Phase(φ) |  | 3 | Out Put | 3.75 (㎾)
Total Head(m) | 34 |  | Pole(P) |  | 2 | Freq | 60 (Hz)
suct,disch(A) | 65A / 40A |  | Volt(V) |  | 220/380 | Maker | HANIL
Model | HE-3SF-40-125/3.06 |  | Customer
OY
※ PERFORMANCE DATA (Test by Ks B 6301)
Capacity(L/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | In put(kw) | Vol tage(V) | Current(A)
0 | 36.2 | 0.959 | 0 | 0 | 1.096 | 380 | 2.86
181 | 35 | 1.7229 | 1.0326 | 59.935 | 1.969 | 380 | 3.88
355 | 30 | 2.3476 | 1.736 | 73.9449 | 2.683 | 380 | 4.88
469 | 25 | 2.5944 | 1.9112 | 73.6661 | 2.965 | 380 | 5.29
555 | 20 | 2.8175 | 1.8093 | 64.2165 | 3.22 | 380 | 5.55
624 | 15 | 2.8053 | 1.5257 | 54.3866 | 3.206 | 380 | 5.65
694 | 10.1 | 2.8131 | 1.1425 | 40.6143 | 3.215 | 380 | 5.67
※ PERFORMANCE CURVE