## 펌프외형도
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 양 수 량(L/min) |  | 80 (20m) |  | BOOSTER | 모 터 부 | 정 격 출 력 (㎾) |  | 0.75
| 흡 상 고 (m) |  | 0 |  |  |  | 정 격 전 압 (V) |  | 380
| 압 상 고 (m) |  | 27 |  |  |  | 정 격 주 파 수 (Hz) |  | 60
| 흡 입 경 (mm) |  | 32A |  |  |  | 회 전 수 (rpm) |  | 3400
| 토 출 경 (mm) |  | 32A |  |  |  | 모 터 Type |  | 삼상 2극
각 부 치 수(mm)
| A | B | C | D | E | F | G | 질소탱크
| 280 | 356 | 90 | 260 | 418 | 431 | 592 | 19L(횡형)
[7 empty] | PUMP TYPE |  | BOOSTER
[7 empty] | 형 식 |  | HIE1(S)-3201-3T

## data sheet
PUMP DATA SHEET
Model | HIE1(S)-3201-3T | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■ In, □ out
OPERATING CONDITION
Liquid | Water | Flow | 80 L/min at Ht=20m
Pumping Temp | 0℃ ~ 80℃ | Suct. Head | 0m
Specific Gravity |  | Disch. Head | 27m
Vapor Pressure | ㎏/㎠A | Total Head | 27m
Viscosity | cP
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
□ Horizontal ■ Vertical |  | Efficiency |  |  | (Parts' Name) | Symbol㉿
Number of Stages | 2 Stage | Rated Power |  |  | Impeller | STS - 304
Speed | 3400 rpm | NPSHre | mAq |  | Impeller cover | STS - 304
Rotation | ■ CW, □ CCW (viewed from motor fan cover) |  |  |  | Shaft | STS - 316
Flange | Size(Dia) | Rating | Face | Position | Casing | GC-200/(STS - 304)
Suction | 32A |  | ■ FF, □ RF | □TOP ■Side | Suct. Flange | GC-200/(STS - 304)
Discharge | 32A |  | ■ FF, □ RF | □TOP ■Side | Disch. Flange | GC-200/(STS - 304)
Impeller Type | close Type | ■ Single Suct □ Double Suct |  | HYDROSTATIC | Guide Vane | STS - 304
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | 10 ㎏/㎠ | 3 Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Pressure Tank | 10 ㎏/㎠ | 3 Min
Shaft Sleeve | □ Yes ■ No
Mounting | ■ Foot □ Centerline |  |  | TESTING
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) | (self test) | (Witness)
Cooling | □ Stuff. Box □ B/R Housing ■ Fan Cooling |  |  | Run Perform | ■ Yes □ No | □ Yes □ No
R Bearing | 6203 zz c3 | F Bearing | 6205 zz c3 | Hydrostatic | ■ Yes □ No | □ Yes □ No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 380 | 3 | 60 | Impeller
Maker | HANIL PUMP Co., Ltd. |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 0.75kW |  |  |  | Casing Ring
Pole&Speed | 2P 3400rpm | Insulation Class | ■ F □ B |  | Bearing(R+F)
ACCESSORIES |  |  |  |  | M/Seal
■ Base Plate | □ Cast Iron □ Plastic ■ Steel Plate |  |  |  | Oil Seal
□ Unions
□ Coupling | □ Sun Flex □ Wood □ Grid □ No |  |  |  | Coupling
□ Pressure Gauge | □ Suct. Vacuum □ Suct. Compound □ Disch. Press ■ No |  |  |  | Coupling Rubber
■ Plug for priming & Screw for Drain |  |  |  |  | Name Plate
Mechnical Seal | Maker | EKK | Model & Size | φ12 | WEIGHT
| Type | EE220-012 | Cooler | □ Yes ■ No | Pump/Bed | Kg
□ Companoion Flange |  |  |  |  | Driver | Kg
□ Special Tools |  |  |  |  | Total Wt | 63 Kg

## test report
PUMP TEST REPORT
※SPELIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION(INPUT POWER)
Capacity(L/min) | 80 (20m) |  | Phase(φ) |  | 3 | Out Put
Total Head(m) | 27 |  | Pole(p) |  | 2 | Freq | 60 (Hz)
suct,disch(mm) | 32A |  | Volt(v) |  | 380 | Maker | HANIL
Model | HIE1(S)-3201-3T |  | Customer
※ PERFOR MANCE DATA (Test by Ks B 6301)
Capacity(L/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | out put(kw) | Vol tage(V) | Current(A)
0 | 29.5 | 0.35658 | 0 | 0 | 0.566 | 380
51 | 25 | 0.49014 | 0.18745 | 38.2442 | 0.778 | 380
100 | 20 | 0.60543 | 0.29992 | 49.5383 | 0.961 | 380
126 | 15 | 0.64386 | 0.29585 | 45.9487 | 1.022 | 380
144 | 10 | 0.65016 | 0.23146 | 35.6005 | 1.032 | 380
160 | 5 | 0.65079 | 0.1304 | 20.0372 | 1.033 | 380
※ PERFOR MANCE CURVE
|  | 7.7 |  |  | 11