## 펌프외형도
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 정 격 양 수 량 | 260L/min(8m) |  | 개별인버터펌프 | 모 터 부 | 정 격 출 력 (㎾) |  | 0.9
| 흡 상 고 (m) | 6 |  |  |  | 정 격 전 압 (V) |  | 220
| 압 상 고 (m) | 18 |  |  |  | 정 격 주 파 수 (Hz) |  | 60
| 흡 입 경 (A) | 50 |  |  |  | 회 전 수 (rpm) |  | 3400
| 토 출 경 (A) | 40 |  |  |  | 모 터 Type |  | 단상 2극
각 부 치 수(mm)
A | B | C | D | E | F | G | H | I | J
240 | Φ130 (4L) | 270 | 237 | 241 | 410 | 367 | 184 | 220 | 250
[6 empty] | PUMP TYPE |  | 개별인버터펌프
[6 empty] | 형 식 |  | HIE1-1000SS

## data sheet
PUMP DATA SHEET
Model | HIE1-1000SS | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■ In, □ out
OPERATING CONDITION
Liquid | Water | Flow | 260 L/min at Ht=8m
Pumping Temp | 0℃ ~ 40℃ | Suct. Head | 6m
Specific Gravity |  | Disch. Head | 18m
Vapor Pressure | ㎏/㎠A | Total Head | 24m
Viscosity | cP
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
■ Horizontal □ Vertical |  | Efficiency |  |  | (Parts' Name) | Symbol㉿
Number of Stages | Stage | Rated Power |  |  | Impeller | STS-304
Speed | 3400 rpm | NPSHre | mAq |  | Impeller cover | -
Rotation | □ CW, ■ CCW (viewed from pump head) |  |  |  | Shaft | SM20C+STS316
Flange | Size(Dia) | Rating | Face | Position | Casing | PP
Suction | 50A |  | □ FF, □ RF | □TOP ■Side | Suct. Flange | PP
Discharge | 40A |  | □ FF, □ RF | ■TOP □Side | Disch. Flange | -
Impeller Type | close Type | ■ Single Suct □ Double Suct |  | HYDROSTATIC | Guide Vane | PPS
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | 5 ㎏/㎠ | 3 Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Pressure Tank | ㎏/㎠ | Min
Shaft Sleeve | □ Yes ■ No
Mounting | ■ Foot □ Centerline |  |  | TESTING
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) | (self test) | (Witness)
Cooling | □ Stuff. Box □ B/R Housing ■ Fan Cooling |  |  | Run Perform | ■ Yes □ No | □ Yes □ No
R Bearing | 6203 zz | F Bearing | 6204 zz | Hydrostatic | ■ Yes □ No | □ Yes □ No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller
Maker | HANIL PUMP Co., Ltd. |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 0.9 kW |  |  |  | Casing Ring
Pole&Speed | 2P 3400rpm | Insulation Class | ■ F □ E |  | Bearing(R+F)
ACCESSORIES |  |  |  |  | M/Seal
■ Base Plate | □ Cast Iron □ Plastic ■ Steel Plate |  |  |  | Oil Seal
□ Unions
□ Coupling | □ Sun Flex □ Wood □ Grid ■ No |  |  |  | Coupling
□ Pressure Gauge | □ Suct. Vacuum □ Suct. Compound □ Disch. Press ■ No |  |  |  | Coupling Rubber
■ Plug for priming & Screw for Drain |  |  |  |  | Name Plate
Mechnical Seal | Maker | EAGLE | Model & Size | φ14 | WEIGHT
| Type | EA103-014SH | Cooler | □ Yes ■ No | Pump/Bed | Kg
□ Companoion Flange |  |  |  |  | Driver | Kg
□ Special Tools |  |  |  |  | Total Wt | 32 Kg

## test report
PUMP TEST REPORT
※SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(L/min) | 310 |  | Phase(φ) |  | 1 | Out Put
Total Head(m) | 24 |  | Pole(p) |  | 2 | Freq | 60 (Hz)
suct,disch(A) | 50, 40 |  | Volt(v) |  | 220 | Maker | HANIL
Model | HIE1-1000SS |  | Customer
※ PERFOR MANCE DATA (Test by Ks B 6301)
Capacity(L/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | out put(kW) | Vol tage(V) | Current(A)
0 | 25 | 0.78817 | 0 | 0 | 1.017 | 220
114 | 20 | 0.9579 | 0.37164 | 38.7974 | 1.236 | 220
177 | 16 | 1.0796 | 0.46162 | 42.759 | 1.393 | 220
230 | 12 | 1.1834 | 0.44988 | 38.0151 | 1.527 | 220
274 | 8 | 1.2408 | 0.3573 | 28.7962 | 1.601 | 220
317 | 3.5 | 1.2718 | 0.18085 | 14.2202 | 1.641 | 220
※ PERFOR MANCE CURVE