## 펌프외형도
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 양수량 (L/min) | 90(3m) | 모 터 부 | 정 격 출 력 (㎾) | 0.18
| 흡 상 고 (m) | - |  | 정 격 전 압 (V) | 220/380겸용
| 압 상 고 (m) | 9 |  | 정격 주파수 (Hz) | 60
| 흡 입 경 (mm) | - |  | 회 전 수 (rpm) | 3400
| 토 출 경 (mm) | 15A |  | 모 터 Type | 삼상 2극
(단위 : mm)
|  |  |  | PUMP Type | 쿨런트 펌프
|  |  |  | 형 식 | HVCP-180-T

## 펌프단면도
펌 프 단 면 도
NO | 부 품 명 | 재 질 | NO | 부 품 명 | 재 질
1 | 모터프레임 | ALDC | 9 | 홀 더 | GC-200
2 | 터미널블럭 | ALDC | 10 | 베어링 캡 | SECC
3 | 터미널커버 | PET | 11 | 베어링 | 6201zz
4 | 회전방향점검창 | NBR 60 | 12 | 케이싱 | GC-200
5 | 베 어 링 | 6201zz | 13 | 임펠러 | powder steel
6 | 스테이터조립 | S-60 | 14
7 | 로터DC | S-60 | 15
8 | 모터샤프트 | SM45C | 16
|  |  | PUMP Type |  | 쿨런트 펌프
|  |  | 형 식 |  | HVCP-180-T

## data sheet
PUMP DATA SHEET
Model | HVCP-180-T | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■ In, □ out
OPERATING CONDITION
Liquid | Cutting Oil | Flow | 90 L/min at Ht = 3m
Pumping Temp | 0℃ ~40℃ | Suct. Head | -
Specific Gravity |  | Disch. Head | 9 m
Vap.Pressure | ㎏/㎠A | Total Head | 9 m
Viscosity | 2~32 cSt
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
□ Horizontal ■ Vertical |  | Efficiency |  |  | (Parts' Name) | Symbol㉿
Number of Stages | 1 Stage | Rated Power | 180 W |  | Impeller | powder steel
Speed | 3400rpm | NPSHr | mAq |  | Shaft | SM45C
Rotation | □ CW, ■ CCW (viewed from motor fan cover) |  |  |  | Casing | GC-200
Flange | Size(Dia) | Rating | Face | Position | Motor Frame | ALDC
Suction | - |  | □ FF, □ RF | □TOP □ Side | Holder | GC-200
Discharge | 15A |  | □ FF, □ RF | □TOP ■ Side | Impeller Cover | GC-200
Impeller Type | Volute Type | □ Single Suct □ Double Suct |  | HYDROSTATIC
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | ㎏/㎠ | Min
Shaft Seal | □ G/Packing □ M/Seal |  |  | Pressure Tank | ㎏/㎠ | Min
Shaft Sleeve | □ Yes ■ No
Mounting | ■ Foot □ Centerline |  |  | TESTING
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) | (self test) | (Witness)
Cooling | □ Stuff. Box □ B/R Housing □ Fan Cooling |  |  | Run Perform | ■ Yes □ No | □ Yes ■ No
R. Bearing | 6201zz | F. Bearing | 6201zz | Hydrostatic | ■ Yes □ No | □ Yes ■ No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220/380 | 3 | 60 | Impeller
Maker | HANIL PUMP LTD,. |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Casing
Power | 180W |  |  |  | Motor Frame
Pole&Speed | 2P 3400rpm | Insulation Class | F |  | Holder
ACCESSORIES |  |  |  |  | Bearing(R+F)
□ Base Plate | □ Cast Iron □ Plastic □ Steel Plate ■ No |  |  |  | Bearing(R+F)
□ Unions |  |  |  |  | Name Plate
□ Coupling | □ Sun Flex □ Wood □ Grid ■ No |  |  |  | M/seal
□ Pressure Gauge | □ Suct. Vacuum □ Suct. Compound □ Disch. Press ■ No
□ Plug for priming & Screw for Drain
Mechnical Seal | Maker | - | Model & Size | - | WEIGHT
| Type | - | Cooler | □ Yes ■ No | Pump/Bed | Kg
□ Companion Flange |  |  |  |  | Driver | Kg
□ Special Tools |  |  |  |  | Total Wt. | 11 Kg

## test report
PUMP TEST REPORT
※SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(L/min) | 90(3m) |  | Phase(φ) |  | 3 | Out Put | 0.18(㎾)
Total Head(m) | 9 |  | Pole(p) |  | 2 | Freq | 60(Hz)
Suct/Disch(mm) | - / 15A |  | Volt(v) |  | 220 / 380 | Maker | HANIL
Model | HVCP-180-T |  | Customer
※ PERFORMANCE DATA (Test by Ks B 6301)
Capacity(ℓ/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | output(kw) | Voltage(V) | Current(A)
0 | 10.5 | 0.1043 | 0 | 0 | 0.14 | 220 | 0.48
56.789 | 7 | 0.16092 | 0.064796 | 40.2661 | 0.216 | 220 | 0.66
83.1 | 4 | 0.2004 | 0.054181 | 27.0359 | 0.269 | 220 | 0.79
90.3 | 3 | 0.21307 | 0.044157 | 20.724 | 0.286 | 220 | 0.84
94.7 | 0.12 | 0.2153 | 0.0018523 | 0.86033 | 0.289 | 220 | 0.85
※ PERFORMANCE CURVE(ISO 9906 ANNEX A)