## 펌프외형도
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 양 수 량(L/min) |  | 60 (34.5m) |  | BOOSTER | 모 터 부 | 정 격 출 력 (㎾) |  | 0.75
| 흡 상 고 (m) |  | 0 |  |  |  | 정 격 전 압 (V) |  | 220
| 압 상 고 (m) |  | 44 |  |  |  | 정 격 주 파 수 (Hz) |  | 60
| 흡 입 경 (mm) |  | 25A |  |  |  | 회 전 수 (rpm) |  | 3450
| 토 출 경 (mm) |  | 25A |  |  |  | 모 터 Type |  | 단상 2극
각 부 치 수(mm)
A | B | C | D | E | F | G | H | I | J
559.5 | 320 | 100 | 250 | 137 | 191 | 180 | 210 | 75 | 25A
[7 empty] | PUMP TYPE |  | BOOSTER
[7 empty] | 형 식 |  | AVS-20401

## 펌프단면도
펌 프 단 면 도
| NO | 부품명 | 재질 | 수량
| 1 | 케이싱 하 | GC-200 | 1
| 2 | 케이싱 조립 | STS-304 | 1
| 3 | 내판 A | STS-304 | 1
| 4 | 흡수본체 조립 | STS-304 | 1
| 5 | 가이드베인 조립 | STS-304 | 2
| 6 | 가이드베인 하조립 | STS-304 | 1
| 7 | 임펠러 조립 | STS-304 | 4
| 8 | 송수본체 조립 | STS-304 | 1
| 9 | 홀더 부착판조립 | STS-304 | 1
| 10 | 보호판 | STS-304 | 2
| 11 | 커플링 | 아연도금 | 2
| 12 | 홀더 | GC-200 | 1
| 13 | 모터조립 | 0.75kW | 1
| 14 | 렌치볼트 | 아연도금 | 4
| 15 | 핀 | 아연도금 | 1
| 16 | 에어벤트 | 황동 | 1
| 17 | 샤프트 | STS-316 | 1
| 18 | 메카니컬씰 | CARBON+SIC | 1
| 19 | 스톱링 | STS-304 | 1
| 20 | 스톱퍼 | STS-304 | 1
| 21 | 부싱A | STS-304 | 6
| 22 | 베어링부싱 | tungsten carbide | 1
| 23 | 부싱B | STS-304 | 1
| 24 | 부싱C | STS-304 | 1
| 25 | 오링 | NBR | 2
| 26 | 와셔 | STS-304 | 1
| 27 | 볼트 | STS-304 | 1
| 28 | 물빼기캡 | STS-304 | 1
| 29 | 패킹 A | NBR | 1
| 30 | 물빼기 소켓 | STS-304 | 1
| 31 | 패킹 B | NBR | 1
| 32 | 너트 | 아연도금 | 4
| 33 | 와셔 | 아연도금 | 4
| 34 | 스텃볼트 | SCM열처리 | 4
35
| PUMP Type |  | Vertical Multistage Pump
| 형 식 |  | AVS-20401

## data sheet
PUMP DATA SHEET
Model | AVS-20401 | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■ In, □ out
OPERATING CONDITION
Liquid | Water | Flow | 60 L/min at Ht=34.5 m
Pumping Temp | 0℃ ~ 80℃ | Suct. Head | 0 |  | m
Specific Gravity |  | Disch. Head | 44 |  | m
Vapor Pressure | ㎏/㎠A | Total Head | 44 |  | m
Viscosity | cP
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
□ Horizontal ■ Vertical |  | Efficiency |  |  | (Parts' Name) | Symbol㉿
Number of Stages | 4 Stage | Rated Power | 0.75 kW |  | Impeller | STS - 304
Speed-rpm | 3450 | NPSHre | mAq |  | Case | STS - 304
Rotation | ■ CW, □ CCW (viewed from motor fan cover) |  |  |  | Shaft | STS - 316
Flange | Size(Dia) | Rating | Face | Position | Casing | STS - 304
Suction | 25A |  | ■ FF, □ RF | □TOP ■Side | Suct. Flange | STS - 304
Discharge | 25A |  | ■ FF, □ RF | □TOP ■Side | Disch. Flange | STS - 304
Impeller Type | close Type | ■ Single Suct □ Double Suct |  | HYDROSTATIC | Guide Vane | STS - 304
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | 10 ㎏/㎠ | 3 Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Pressure Tank | 10 ㎏/㎠ | 3 Min
Shaft Sleeve | □ Yes ■ No
Mounting | ■ Foot □ Centerline |  |  | TESTING
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) | (self test) | (Witness)
Cooling | □ Stuff. Box □ B/R Housing ■ Fan Cooling |  |  | Run Perform | ■ Yes □ No | □ Yes □ No
R Bearing | 6203 zz c3 | F Bearing | 6205 zz c3 | Hydrostatic | ■ Yes □ No | □ Yes □ No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller
Maker | HANIL PUMP Co., Ltd. |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 0.75 |  | kW |  | Casing Ring
Pole&Speed | 2P 3450rpm | Insulation Class | ■ F □ B |  | Bearing(R+F)
ACCESSORIES |  |  |  |  | M/Seal
■ Base Plate | □ Cast Iron □ Plastic ■ Steel Plate |  |  |  | Oil Seal
□ Unions
□ Coupling | □ Sun Flex □ Wood □ Grid □ No |  |  |  | Coupling
□ Pressure Gauge | □ Suct. Vacuum □ Suct. Compound □ Disch. Press ■ No |  |  |  | Coupling Rubber
■ Plug for priming & Screw for Drain |  |  |  |  | Name Plate
Mechnical Seal | Maker | EKK | Model & Size | φ12 | WEIGHT
| Type | EE220-012 | Cooler | □ Yes ■ No | Pump/Bed | Kg
□ Companoion Flange |  |  |  |  | Driver | Kg
□ Special Tools |  |  |  |  | Total Wt.(net) | 39 Kg

## test report
PUMP TEST REPORT
※SPELIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(L/min) | 60 (34.5m) |  | Phase(φ) |  | 1 | Out Put(kW) | 0.75
Head(m) | 44 |  | Pole(p) |  | 2 | Freq(Hz) | 60
suct,disch(mm) | 25A |  | Volt(v) |  | 220 | Maker | HANIL
Model | AVS-20401 |  | Customer
※ PERFOR MANCE DATA (Test by Ks B 6301)
Capacity(L/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | out put(kw) | Vol tage(V) | Current(A)
0 | 44.2 | 0.27941 | 0 | 0 | 0.361 | 220
33.7 | 43 | 0.48607 | 0.2362 | 48.5943 | 0.628 | 220
58.8 | 36 | 0.59598 | 0.34504 | 57.8943 | 0.77 | 220
72.9 | 30 | 0.62926 | 0.35648 | 56.6506 | 0.813 | 220
83 | 24 | 0.64165 | 0.3247 | 50.6036 | 0.829 | 220
102.2 | 2.3 | 0.58901 | 0.038315 | 6.5049 | 0.761 | 220
※ PERFOR MANCE CURVE
|  | 7.7 |  |  | 11