## OUTSIDE DRAWING
OUTSIDE DRAWING
SPECIFICATION FOR PUMP & MOTOR
PUMP | Capacity(L/min) |  | 60 (81m) |  | BOOSTER | MOTOR | Power (㎾) |  | 1.5
| Suc. Head (m) |  | 0 |  |  |  | Volt. (V) |  | 220
| Dis. Head (m) |  | 99 |  |  |  | Freq. (Hz) |  | 60
| Suc.Size (mm) |  | 25A |  |  |  | Speed (rpm) |  | 3450
| Dis. Size (mm) |  | 25A |  |  |  | Phase | Pole | 1 | 2
Outline Dimensions(mm)
A | B | C | D | E | F | G | H | I | J
692.5 | 420 | 100 | 250 | 137 | 191 | 180 | 210 | 75 | 25A
[7 empty] | PUMP TYPE |  | BOOSTER
[7 empty] | MODEL |  | AVS-20902

## SECTIONAL DRAWING
SECTIONAL DRAWING
| NO | Partname | meterial | Q'ty
| 1 | Under Casing | GC-200 | 1
| 2 | Casing assy | STS-304 | 1
| 3 | Inner plate A | STS-304 | 1
| 4 | Suction chamber | STS-304 | 1
| 5 | Diffuser | STS-304 | 7
| 6 | Under Diffuser | STS-304 | 1
| 7 | Impeller | STS-304 | 9
| 8 | Discharge chamber | STS-304 | 1
| 9 | Holder plate | STS-304 | 1
| 10 | Coupling guard | STS-304 | 2
| 11 | Coupling | 아연도금 | 2
| 12 | Holder | GC-200 | 1
| 13 | Motor | 1.5kW | 1
| 14 | Cap screw | 아연도금 | 4
| 15 | Pin | 아연도금 | 1
| 16 | Air vent | 황동 | 1
| 17 | Shaft | STS-316 | 1
| 18 | Mechanical seal | CARBON+SIC | 1
| 19 | Stop ring | STS-304 | 1
| 20 | Stopper | STS-304 | 1
| 21 | Bush A | STS-304 | 16
| 22 | T/C bush | tungsten carbide | 1
| 23 | Bush B | STS-304 | 1
| 24 | Bush C | STS-304 | 1
| 25 | Case packing | NBR | 2
| 26 | Washer | STS-304 | 1
| 27 | Lock bolt | STS-304 | 1
| 28 | Drain cap | STS-304 | 1
| 29 | Drain cap o-ring A | NBR | 1
| 30 | Drain sockrt | STS-304 | 1
| 31 | Drain cap o-ring B | NBR | 1
| 32 | Nut | 아연도금 | 4
| 33 | Washer | 아연도금 | 4
| 34 | Tie-bolt | SCM열처리 | 4
35
| PUMP Type |  | BOOSTER
| MODEL |  | AVS-2 common part
AVS-20902

## Data Sheet
PUMP DATA SHEET
Model | AVS-20902 | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■ In, □ out
OPERATING CONDITION
Liquid | Water | Flow | 60 (81m) |  | L/min
Pumping Temp | 0℃ ~ 80℃ | Suct. Head | 0
Specific Gravity |  | Disch. Head | 99
Vapor Pressure | ㎏/㎠A | Total Head | 99
Viscosity | 1 cP
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
□ Horizontal ■ Vertical |  | Efficiency |  |  | (Parts' Name) | Symbol㉿
Number of Stages | 9 Stage | Rated Power | 1.5 |  | Impeller | STS - 304
Speed | 3450 | NPSHre | mAq |  | Impeller cover | STS - 304
Rotation | ■ CW, □ CCW (viewed from motor) |  |  |  | Shaft | STS - 316
Flange | Size(Dia) | Rating | Face | Position | Casing | GC - 200
Suction | 25A |  | ■ FF, □ RF | □TOP ■Side | Suct. Flange | GC - 200
Discharge | 25A |  | ■ FF, □ RF | □TOP ■Side | Disch. Flange | GC - 200
Impeller Type | close Type | ■ Single Suct □ Double Suct |  | HYDROSTATIC | Guide Vane | STS - 304
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | 10 ㎏/㎠ | 3 Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Pressure Tank | 10 ㎏/㎠ | 3 Min
Shaft Sleeve | □ Yes ■ No
Mounting | ■ Foot □ Centerline |  |  | TESTING
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) | (self test) | (Witness)
Cooling | □ Stuff. Box □ B/R Housing ■ Fan Cooling |  |  | Run Perform | ■ Yes □ No | □ Yes □ No
R Bearing | 6203 zz c3 | F Bearing | 6205 zz c3 | Hydrostatic | ■ Yes □ No | □ Yes □ No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller
Maker | HANIL PUMP Co., Ltd. |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 1.5 |  |  |  | Casing Ring
Pole&Speed | 2P 3450rpm | Insulation Class | ■ F □ E |  | Bearing(R+F)
ACCESSORIES |  |  |  |  | M/Seal
■ Base Plate | □ Cast Iron □ Plastic ■ Steel Plate |  |  |  | Oil Seal
□ Unions
□ Coupling | □ Sun Flex □ Wood □ Grid □ No |  |  |  | Coupling
□ Pressure Gauge | □ Suct. Vacuum □ Suct. Compound □ Disch. Press ■ No |  |  |  | Coupling Rubber
■ Plug for priming & Screw for Drain |  |  |  |  | Name Plate
Mechnical Seal | Maker | EKK | Model & Size | φ12 | WEIGHT
| Type | EE220-012 | Cooler | □ Yes ■ No | Pump/Bed | kg
□ Companoion Flange |  |  |  |  | Driver | kg
□ Special Tools |  |  |  |  | Total Wt. | 45.5 kg

## Test Report
PUMP TEST REPORT
※SPELIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(L/min) | 60 (81m) |  | Phase(φ) |  | 1 | POWER(kW) | 1.5
Total Head(m) | 99 |  | Pole(p) |  | 2 | Freq(Hz) | 60
suct,disch(mm) | 25A |  | Volt(v) |  | 220 | Maker | HANIL
Model | AVS-20902 |  | Customer
※ PERFOR MANCE DATA (Test by Ks B 6301)
Capacity(L/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | out put(kw) | Vol tage(V) | Current(A)
0 | 101 | 0.50403 | 0 | 0 | 0.608 | 380 | 1.66
41.5 | 95 | 1.1059 | 0.64263 | 58.1097 | 1.334 | 380 | 2.49
60 | 83 | 1.2883 | 0.81174 | 63.0103 | 1.554 | 380 | 2.79
71.3 | 73 | 1.367 | 0.8484 | 62.0619 | 1.649 | 380 | 2.93
95.5 | 40 | 1.3902 | 0.62266 | 44.7882 | 1.677 | 380 | 2.98
101.4 | 2.2 | 1.2485 | 0.036362 | 2.9125 | 1.506 | 380 | 2.73
※ PERFOR MANCE CURVE