## OUTSIDE DRAWING
OUTSIDE DRAWING
SPECIFICATION FOR PUMP & MOTOR
PUMP | Capacity(L/min) |  | 110 (32m) |  | BOOSTER | MOTOR | Power (㎾) |  | 1.1
| Suc. Head (m) |  | 0 |  |  |  | Volt. (V) |  | 220
| Dis. Head (m) |  | 42 |  |  |  | Freq. (Hz) |  | 60
| Suc.Size (mm) |  | 32A |  |  |  | Speed (rpm) |  | 3450
| Dis. Size (mm) |  | 32A |  |  |  | Phase | Pole | 3 | 2
Outline Dimensions(mm)
A | B | C | D | E | F | G | H | I
190 | 220 | 113 | 317 | 610 | 130 | 417 | 32A | 32A
Outline Dimensions(mm) H: PUMP TYPE | BOOSTER
Outline Dimensions(mm) H: MODEL | AHIE1S-30401
drawing model ; AHIE1S-30401

## SECTIONAL DRAWING
SECTIONAL DRAWING
NO | Partname | meterial | Q'ty | NO | Partname | meterial | Q'ty
1 | Air vent | Bronze | 1 | 18 | Fan ass'y | - | 1
2 | Suc.casing | STS-304 | 1 | 19 | Drain cap | STS-304 | 1
3 | Suc. chamber | STS-304 | 1 | 20 | O-ring | NBR | 1
4 | Under Diffuser | STS-304+T/C | 1 | 21 | Bolt | STS-304 | 1
5 | Diffuser | STS-304 | 2 | 22 | Washer | STS-304 | 1
6 | Impeller | STS-304 | 4 | 23 | Bush A | STS-304 | 7
7 | Stopper | STS-304 | 1 | 24 | Bush B | STS-304 | 1
8 | Mechanical seal | HSS-12 | 1 | 25 | T/C bush | T/C | 1
9 | dis.casing | STS-304 | 1 | 26 | Bush C | STS-304 | -
10 | bearing | 6205zz | 1 | 27 | Washer | STS-304 | 3
11 | Stopring | SPCC | 1 | 28 | Gasket | Non-asbesto | 5
12 | Terminal box | ALDC | 1 | 29 | shaft | STS-304 | 1
13 | Terminal cover | ALDC | 1 | 30 | bed | SPCC | 1
14 | Motorframe ass'y | ALDC+STEEL | 1 | 31 | bolt | - | 4
15 | rotor | ALDC+STEEL | 1 | 32 | bearing | 6204zz | 1
16 | Motor cover | GC-200 | 1 | 33 | bolt | SCM | 4
17 | fan cover | SPCC | 1 | 34 | S/P Washer | - | 4
|  |  |  | PUMP Type |  | BOOSTER
|  |  |  | MODEL |  | AHIE1S-30401
drawing model ; AHS-30602-T

## Data Sheet
PUMP DATA SHEET
Model | AHIE1S-30401 |  | Title |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■ In, □ out
OPERATING CONDITION
Liquid | Water | Flow | 110 (32m) |  | L/min
Pumping Temp | 0℃ ~ 80℃ | Suct. Head | 0
Specific Gravity |  | Disch. Head | 42
Vapor Pressure | ㎏/㎠A | Total Head | 42
Viscosity | 1 cP
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
■ Horizontal □ Vertical |  | Efficiency |  |  | (Parts' Name) | Symbol㉿
Number of Stages | 4 Stage | Rated Power | 1.1 |  | Impeller | STS - 304
Speed | 3450 | NPSHre | mAq |  | Diffuser | STS - 304
Rotation | ■ CW, □ CCW (viewed from motor) |  |  |  | Shaft | STS - 316
Flange | Size(Dia) | Rating | Face | Position | Suct. Casing | STS - 304
Suction | 32A |  | □ FF, □ RF | □TOP ■Side | Disch. Casing | STS - 304
Discharge | 32A |  | □ FF, □ RF | □TOP ■Side
Impeller Type | close Type | ■ Single Suct □ Double Suct |  | HYDROSTATIC
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | 10 ㎏/㎠ | 3 Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Pressure Tank | 10 ㎏/㎠ | 3 Min
Shaft Sleeve | □ Yes ■ No
Mounting | ■ Foot □ Centerline |  |  | TESTING
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) | (self test) | (Witness)
Cooling | □ Stuff. Box □ B/R Housing ■ Fan Cooling |  |  | Run Perform | ■ Yes □ No | □ Yes □ No
R Bearing | 6204 zz c3 | F Bearing | 6205 zz c3 | Hydrostatic | ■ Yes □ No | □ Yes □ No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220 | 3 | 60 | Impeller
Maker | HANIL PUMP Co., Ltd. |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 1.1 |  |  |  | Casing Ring
Pole&Speed | 2P 3450rpm | Insulation Class | ■ F □ E |  | Bearing(R+F)
ACCESSORIES |  |  |  |  | M/Seal
■ Base Plate | □ Cast Iron □ Plastic ■ Steel Plate |  |  |  | Oil Seal
□ Unions
□ Coupling | □ Sun Flex □ Wood □ Grid □ No |  |  |  | Coupling
□ Pressure Gauge | □ Suct. Vacuum □ Suct. Compound □ Disch. Press ■ No |  |  |  | Coupling Rubber
■ Plug for priming & Screw for Drain |  |  |  |  | Name Plate
Mechnical Seal | Maker | EKK | Model & Size | φ12 | WEIGHT
| Type | EE220-012 | Cooler | □ Yes ■ No | Pump/Bed | kg
□ Companoion Flange |  |  |  |  | Driver | kg
□ Special Tools |  |  |  |  | Total Wt. | 21.5 kg

## Test Report
PUMP TEST REPORT
※SPELIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(L/min) | 110 (32m) |  | Phase(φ) |  | 3 | POWER(kW) | 1.1
Total Head(m) | 42 |  | Pole(p) |  | 2 | Freq(Hz) | 60
suct,disch(mm) | 32A |  | Volt(v) |  | 220 | Maker | HANIL
Model | AHIE1S-30401 |  | Customer
※ PERFOR MANCE DATA (Test by Ks B 6301)
Capacity(L/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | out put(kw) | Vol tage(V) | Current(A)
0 | 42.4 | 0.47278 | 0 | 0 | 0.614 | 220
48 | 40 | 0.67375 | 0.31296 | 46.4505 | 0.875 | 220
110 | 32 | 0.93093 | 0.57376 | 61.633 | 1.209 | 220
153.3 | 20 | 0.97328 | 0.49976 | 51.3478 | 1.264 | 220
184.6 | 10 | 0.95634 | 0.3009 | 31.4635 | 1.242 | 220
196.4 | 5.3 | 0.93632 | 0.16967 | 18.1209 | 1.216 | 220
※ PERFOR MANCE CURVE