## 펌프외형도
펌 프 외 형 도
펌 프 사 양
펌 프 부 | 최대양수량 (L/hr) | 2,560(0.5m) | 모 터 부 | 정 격 출 력 (㎾) | 0.25
| 흡 상 고 (m) | 0 |  | 정 격 전 압 (V) | 220
| 압 상 고 (m) | 32 |  | 정 격 주 파 수 (Hz) | 60
| 흡 입 경 (mm) | 20A(3/4") |  | 회 전 수 (rpm) | 3400
| 토 출 경 (mm) | 20A(3/4") |  | 모 터 Type | 단상 2극
(단위 : mm)
|  |  |  | PUMP Type | 웨스코 Type
|  |  |  | 형 식 | MPPH-250-SBDPXNB

## 펌프단면도
펌 프 단 면 도
NO | 부 품 명 | 재 질 | NO | 부 품 명 | 재 질
1 | 모터 조립 | - | 8 | 임펠러 | 황동 단조
2 | 베 드 | P.P | 9 | 케이싱커버 | 노릴
3 | 모터 샤프트 | SM20C+STS410 | 10 | 모터커버 | Aℓ-DC
4 | 홀 더 | Aℓ-DC | 11 | 베어링 | 6200zz
5 | 미캐니컬실 | Carbon+Ceramic | 12 | 베어링 | 6202zz
6 | 케이싱 | BC6 | 13 | 단자대조립 | ABS
7 | 케이싱패킹 | NBR
|  |  | PUMP Type |  | 웨스코 Type
|  |  | 형 식 |  | MPPH-250-SBDPXNB

## data sheet
PUMP DATA SHEET
Model | MPPH-250-SBDPXNB | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■ In, □ out
OPERATING CONDITION
Liquid | Water | Flow | 25 L/min at Ht=12m,(42.6 L/min at Ht=0.5m)
Pumping Temp | 0℃ ~40℃ | Suct. Head | 0
Specific Gravity |  | Disch. Head | 32
Vap.Pressure | ㎏/㎠A | Total Head | 32
Viscosity | cP
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
■Horizontal □Vertical |  | Efficiency | 25.8% |  | (Parts' Name) | Symbol㉿
Number of Stages | 1 Stage | Rated Power | 250 W |  | Impeller | 황동단조
Speed | 3400rpm | NPSHre | mAq |  | Impeller cover | MPPE
Rotation | □ CW, ■ CCW (viewed from pump head) |  |  |  | Shaft | SM20C+STS410
Flange | Size(Dia) | Rating | Face | Position | Casing | BC6
Suction | 20A(3/4') TAP |  | □ FF, □ RF | □TOP ■Side | Suct. Flange | PS 3/4"TAP
Discharge | 20A(3/4') TAP |  | □ FF, □ RF | ■TOP □Side | Disch. Flange | PS 3/4"TAP
Impeller Type | Westco Type | ■ Single Suct □ Double Suct |  | HYDROSTATIC | Guide Vane
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | 5 ㎏/㎠ | 3 Min
Shaft Seal | □ G/Packing ■ M/Seal |  |  | Pressure Tank | ㎏/㎠ | Min
Shaft Sleeve | □ Yes ■ No
Mounting | ■ Foot □ Centerline |  |  | TESTING
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) | (self test) | (Witness)
Cooling | □ Stuff. Box □ B/R Housing ■ Fan Cooling |  |  | Run Perform | ■ Yes □ No | □ Yes ■ No
R. Bearing | 6202zz | F. Bearing | 6200zz | Hydrostatic | ■ Yes □ No | □ Yes ■ No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller
Maker | HANIL PUMP LTD,. |  |  |  | Shaft
Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve
Power | 580W |  |  |  | Casing Ring
Pole&Speed | 2P 3400rpm | Insulation Class | □ E □ B ■ F |  | Bearing(R+F)
ACCESSORIES |  |  |  |  | M/Seal
■ Base Plate | □ Cast Iron ■ Plastic □ Steel Plate
□ Unions
□ Coupling | □ Sun Flex □ Wood □ Grid ■ No
□ Pressure Gauge | □ Suct. Vacuum □ Suct. Compound □ Disch. Press ■ No
■ Plug for priming & Screw for Drain
Mechnical Seal | Maker | PILLAR | Model & Size | φ12 | WEIGHT ※( )는 PH-250W-G임
| Type | HK9A-LM | Cooler | □ Yes ■ No | Pump/Bed | Kg
□ Companoion Flange |  |  |  |  | Driver | Kg
□ Special Tools |  |  |  |  | Total Wt | 6.7 /(6.5) Kg

## test report
PUMP TEST REPORT
※SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION
Capacity(L/min) | 25(12m) |  | Phase(φ) |  | 1 | Out Put(kW) | 0.25
Total Head(m) | 32 |  | Pole(p) |  | 2 | Freq(Hz) | 60
Disch Dia(A,inch) | 20mm(3/4")TAP |  | Volt(V) |  | 220 | Maker | HANIL
Model | MPPH-250-SBDPXNB |  | Customer
※ PERFOR MANCE DATA (Test by Ks B 6301)
Capacity(L/min) | Total Head(m) | Shaft Power(㎾) | Water Power(㎾) | Pump Eff(%) | Motor input(kW) | Vol tage(V) | Current(A)
0 | 42 | 0.504 | 0 | 0 | 0.72 | 220 | 3.29
8.7 | 36 | 0.434 | 0.051052 | 11.763 | 0.62 | 220 | 2.83
17 | 28 | 0.371 | 0.077588 | 20.9132 | 0.53 | 220 | 2.46
32.8 | 12 | 0.266 | 0.064157 | 24.1191 | 0.38 | 220 | 1.85
46 | 1 | 0.217 | 0.007498 | 3.4553 | 0.31 | 220 | 1.51
※ PERFOR MANCE CURVE